## TU1 H2'20
Technology Certification: Tech Update
Infrastructure Solutions (TU1, v1.1, H2 2020)
Summary of Spec Changes
Changes are indicated by yellow blocks in the table. Changes include:
1. Lowered smallest UPS size to 1KVA
2. Added requirements for rack material
3. Added requirements for earthing & bonding
4. Added Management & Monitoring category for datacentre monitoring, management and sensing
Uninterruptible power supplies (UPS)
| UPS_Li1 | UPS_Li2 | UPS_OL1 | UPS_OL2 | UPS_OL3 | UPS_OL4
Profile | Entry-level line-interactive UPS | Midrange line-interactive UPS | Entry-level on-line UPS | Midrange on-line UPS | Advanced on-line UPS | Advanced 3-phase on-line UPS
Design | Line-interactive, pure sinewave |  | On-line double conversion, pure sinewave |  |  | 3-phase on-line double conversion, pure sinewave
Load supported1 | 800W | 1600W | 900W | 2700W | 4.5 KW + | 9 KW +
Power rating | 1 KVA | 2 KVA | 1 KVA | 3 KVA | 5 KVA + | 10 KVA +
Efficiency | 80% |  | 90%
Runtime @ full load | 5 minutes
Max recharge time | 4 hours | 6 hours | 4 hours | 6 hours | 8 hours | 10 hours
Outputs | 4x C13 | 6x C13, 1x C19 | 4x C13 | 6x C13, 1x C19 | 6x C13, 1x C19 or hard-wired | Hard-wired
Input tolerance (while bearing 50% load)2 | 160 - 270VAC, 50Hz ±2% |  | 120 - 270VAC, 50Hz ±15% |  |  | 250 - 450VAC, 50Hz ±15%
Management | USB/Serial, pref SNMP | USB/Serial, SNMP | USB/Serial, pref SNMP | USB/Serial, SNMP
Form factor | Rack-mount/Tower, pref convertible |  |  |  |  | Standalone
Standards | ISO/IEC 60240, EN 55032
OS certification | Windows, Linux |  | Windows, Linux, mainstream hypervisors
Support SLA | 5-year on-site, 4-hour response, NBD fix
Equipment racks
| Rack_Wb | Rack_Net | Rack_Srv | Rack_Env | Rack_AV
Profile | Wall-mount cabinet | Network Cabinet | Server Rack | Environmental Rack | Audiovisual Rack
Rack units | 4 - 15 | 12 - 47 | 12 - 47 | 30+ | 12 - 47
Depth (mm) | 300+ | 600+ | 800+ | 800+ | 600+
Front & rear | Lockable | Lockable, 70% perforation option | Lockable, 70% perforated | Lockable Non-perforated | Lockable
Static ¦ dynamic load | 5kg/u ¦ - | 10kg/u ¦ 8kg/u | 20kg/u ¦ 15kg/u | 20kg/u ¦ 15kg/u | 10kg/u ¦ 8kg/u
Structural material | 16-gauge steel, powder-coated
Standards | IEC 60297-3 family, SANS (electrical), IP20
Support SLA | 5-year on-site, 4-hour response, NBD fix
Management and monitoring
| Infra_Mgmt | Env_Mon
Profile | Infrastructure management tools | Environmental monitoring
Standards | SNMP, SMTP, HTTPS, LDAP
Devices/systems | Data- & switching centre management and monitoring, incl. remote control, sensors, access control
Support SLA | 5-year on-site, NBD fix
Non-ICT components and services
Cabling infrastructure
| Ducting | Trenching | Routing
Profile | Cable ducting | Cable trenching | Cable routing
Requirements | Designed, installed and maintained according to published Government site infrastructure standards
Alternative power infrastructure
| Gen1 | Gen2 | Gen3 | Solar
Profile | Entry-level generator solution | Midrange generator solution | Advanced generator solution | Solar power solution
Requirements | Designed, installed and maintained according to published Government infrastructure power standards
Cooling and ventilation
| AC1 | AC2 | AC3
Profile | Entry-level HVAC solution | Advanced HVAC solution | Advanced HVAC solution
Requirements | Designed, installed and maintained according to published Government site cooling standards
Date: 2020-08-31
Items: 15
Conditions/Notes
1. This Tech Update is to be implemented by H1 2020, and will remain in force until superseded by the next version.
2. Products are certified against the Detail Spec: Infrastructure, not this document. Make sure that the correct version of the detail spec is used for certifications and proposals (the spec header will indicate revision and TU).
3. This document indicates the base spec for Infrastructure, but it does not contain the detail specs, or requirements for upgrades or options. These can be found in the Detail Spec (see above).
4. Once these changes are implemented, the new baseline standard becomes mandatory, and all new products must comply.
5. As per the TCP, all OEMs are required to participate in the TU RFC process: non-response will be interpreted as agreeing with the proposed changes.
6. These specs are minimum requirements, therefore any proposal/capability that equals or improves on the spec will be acceptable.
7. "Pref/Preferred" indicates a non-mandatory requirement, or possible future direction.
Notes
1 Regardless of the KVA rating, the UPS must be sized to meet the specified Watts
2 Acceptable derating at lower voltages will be allowed