## TU1 H1'20
Technical Specifications: Tech Update | [5 empty] | Date: 2019-12-17
Infrastructure Solutions (TU1, v1.1, H1 2020) | [5 empty] | Items: 20
Note 1: This specification is subject to change based on Government requirements, and will be reviewed periodically.
Note 2: The Product Certification Process and Memorandum of Agreement requires OEMs to take the
necessary actions in terms of ensuring product compliance with the new requirements. All other parties
are welcome to provide inputs and comments.
Note 3: The canonical repository for all specs is the detail Infrastructure spec, not this document. All
upgrades, components and more static specifications are contained in the detail spec. This document only
captures the top-line, fast-changing specifications for technology management purposes.
Note 4: The fact that a product is certified does not necessarily mean it is available for procurement on a contract.
In order for a product in this domain to purchased via transversal contract, both the supplier and product must be
explicitly accredited by SITA on the relevant transversal contracts (e.g. Contract 2003/2014 for racks).
Summary of Spec Changes
Changes are indicated by yellow blocks in the table. Changes include:
1. Lowered minimum UPS sizes to 1KVA
2. Added requirements for rack material
3. Added requirements for earthing & bonding
4. Added Management category for SNMP tools
5. Added Monitoring category for datacentre monitoring, management and sensing
Changes to detail Spec are marked in blue in the accompanying Item documents.
Uninterruptible power supplies (UPS)
| UPS_Li1 | UPS_Li2 | UPS_OL1 | UPS_OL2 | UPS_OL3 | UPS_OL4
Profile | Entry-level line-interactive UPS | Midrange line-interactive UPS | Entry-level on-line UPS | Midrange on-line UPS | Advanced on-line UPS | Advanced 3-phase on-line UPS
Design | Line-interactive, pure sinewave |  | Double conversion, pure sinewave |  |  | 3-phase double conversion, pure sinewave
Load supported1 | 800W | 1600W | 900W | 2700W | 4.5 - 18KW | 9 - 36KW
Power rating | 1 KVA | 2 KVA | 1 KVA | 3 KVA | 5 - 20 KVA | 10 - 40 KVA
Efficiency | 80% | 80% | 90% | 90% | 90% | 90%
Runtime @ full load | 5 minutes
Recharge time | 4 hours | 6 hours | 4 hours | 6 hours | 8 hours | 10 hours
Outputs | 4x C13 | 8x C13, 1x C19 | 4x C13 | 8x C13/C19 | 8x C13/C19 or hard-wired | 8x C13/C19 or hard-wired
Input tolerance (while bearing 50% load)2 | 160 - 270VAC, 50Hz ±2% |  | 120 - 270VAC, 50Hz ±5% |  |  | 200 - 415VAC, 50Hz ±5%
Management | USB/Serial, pref SNMP | USB/Serial, SNMP | USB/Serial, pref SNMP | USB/Serial, SNMP
Form factor | Rack-mount/Tower, pref convertible |  |  |  |  | Standalone
Standards | ISO/IEC 60240, EN 55032
OS certification | Windows, Linux |  | Windows, Linux, mainstream hypervisors
Support SLA | 5-year on-site, 4-hour response, NBD fix
1 Regardless of the KVA rating, the UPS must be sized to meet the specified Watts
2 Acceptable derating at lower voltages will be allowed
Equipment racks
| Rack_Wb | Rack_Net | Rack_Srv | Rack_Env | Rack_AV
Profile | Wall-mount cabinet | Network Cabinet | Server Rack | Environmental Rack | Audiovisual Rack
Rack units | 4 - 15 | 12 - 47 | 12 - 47 | 30+ | 12 - 47
Depth (mm) | 300+ | 600+ | 800+ | 800+ | 600+
Front & rear | Lockable | Lockable, 70% perforation option | Lockable, 70% perforated | Lockable Non-perforated | Lockable
Static ¦ dynamic load | 5kg/u ¦ - | 10kg/u ¦ 8kg/u | 20kg/u ¦ 15kg/u | 20kg/u ¦ 15kg/u | 10kg/u ¦ 8kg/u
Structural material | 12-gauge metal, powder-coated
Standards | IEC 60297-3 family, SANS (electrical), IP20
Support SLA | 5-year on-site, 4-hour response, NBD fix
Management and monitoring
| Mgmt | Env_Mon
Profile | System management tools | Environmental monitoring
Standards | SNMP, SMTP, HTTP, LDAP
Devices/systems | Data- & switching centre devices, incl. control, sensors, access control
Support SLA | 5-year on-site, NBD fix
Non-ICT components and services
Cabling infrastructure
| Ducting | Trenching | Routing
Profile | Cable ducting | Cable trenching | Cable routing
Requirements | Designed, installed and maintained according to published Government site infrastructure standards
Alternative power infrastructure
| Gen1 | Gen2 | Gen3 | Solar
Profile | Entry-level generator solution | Midrange generator solution | Advanced generator solution | Solar power solution
Requirements | Designed, installed and maintained according to published Government infrastructure power standards
Design | TBD | TBD | TBD | TBD
Watts | TBD | TBD | TBD | TBD
KVA | TBD | TBD | TBD | TBD
Runtime | TBD | TBD | TBD | TBD
Outputs | TBD | TBD | TBD | TBD
Cooling and ventilation
| AC1 | AC2 | AC3
Profile | Entry-level HVAC solution | Advanced HVAC solution | Advanced HVAC solution
Requirements | Designed, installed and maintained according to published Government site cooling standards
Rules/Conditions/Notes
1. This update to be implemented by H1 2020
2. This TU will remain in force until superseded by the next version.
3. The repository for all detail specifications is the Detail Spec: Infrastructure, not this document. Make sure that
the correct version of the spec is used for model changes or quotations (the header will indicate revision and TU).
4. This document updates the base spec for Infrastructure, but it does not cover the detail specs, or requirements
for upgrades or options. These can be found in the Detail Spec (see above).
5. Once these changes are implemented, the new baseline standard becomes mandatory, and all new products must comply.
6. As per the TCP, all OEMs are required to participate in the TU RFC process: non-response will be interpreted as agreeing
with the proposed changes.
7. These specs are minimum requirements, so any proposal/capability that equals or improves on the spec will be acceptable.
8. Equivalent technologies will be acceptable, as long as functionality is equal or better. Proof of functionality
will be required from OEM.
9. "Pref" indicates a non-mandatory requirement, or possible future direction.