## Conditions
Technology Certification
Infrastructure Solutions
Introduction and Conditions
q | The SITA Technology Certification Process (TCP) is separate from any Request for Bid, Proposal or Quotation process. It is a stand-alone process supporting all RFB/RFP/RFQs issued by Government, in line with SITA's certification mandate as per National Treasury Practice Note 5 of 2009.
q | This technical specification supports the Technology Certification Process (TCP), and while it requires a total solution, it only addresses those solution components explicitly specified, such as the on-site SLA, while excluding, for example, supplier accreditation, which is an SCM function. Components and services not specified as mandatory or optional (e.g. application software) may not be offered under this specification.
q | These specifications form part of the Minimum Interoperability Specification (MIOS) version 6, which mandates SITA to certify ICT goods and services. MIOS v6 refers all hardware-related requirements to the specifications developed as part of the Technology Certification Process (TCP).
q | The specification is for a complete solution, integrated by OEM-certified partners based on the stated client business requirement via transversal contract or an ad hoc RFB/RFP/RFQ. Except where specifically noted in the RFB/RFP/RFQ, solutions must include all components specified, including network and system management, and services including installation and configuration. All other components are specifically excluded from the scope.
q | In terms of National Treasury Practice Note 5 of 2009, any ICT products not certified via this process may not be deployed in Government.
q | Products can only be certified via this process if the OEM has an approved Memorandum of Agreement (MoA) in place with SITA. MoA forms and documentation are available at the Product Certification website www.sita.co.za/prodcert.htm.
q | The fact that a product is certified does not necessarily mean it is available for procurement on a contract (see above). In order for a product in any domain to be purchased via transversal contract, both the supplier and product must be explicitly accredited by SITA for that contract.
q | Any RFP/RFQ, bid or agreement based on this technical specification may not override or replace the technical specification, but build on the TCP process, adhering to all specified conditions and requirements, e.g. mandatory components and the on-site SLA.
q | The technical specification states the minimum requirements of Government. Products or solutions with equivalent or better functionality or performance will be acceptable, subject to proof by the OEM. If the submitted product exceeds the specification, or provides equivalent functionality, always answer "Yes", not "No", in the appropriate field. For example, if the spec requires 2 ports, and the offered product has 3, answer "Yes", and state "3 ports" in the Comments column.
q | A collaborative, Request for Comment-based approach is used to develop and update the technical specifications. OEMs, integrators, suppliers and all other role players are required to participate and provide input whenever a draft Tech Update (TU) is published for comment. Notification of drafts will be sent to a distribution list of role players, and drafts are posted in the RFC section on the Product Certification website at www.sita.co.za/prodcert.htm.
q | The detail technical specification sheets in this document must be completed and submitted by the OEM. No submissions will be accepted if not presented according to the correct process.
q | All required certifications, technical documentation, brochures, product info, etc. must be submitted prior to the evaluation process. Except where specifically required, paper copies need not be submitted; e-mail all soft copies to tas@sita.co.za, share on-line or deliver on portable storage.
q | To ensure that all required information is submitted, OEMs must download, complete and include the Checklist: Product Certification Meeting form with the submission.
q | Ensure that only the latest versions of this specification are used. The specification and other forms are available for download at www.sita.co.za/prodcert.htm.
q | Proof will be required for every line of the technical specification. Ensure that all requirement information is available for the evaluation meeting, otherwise the product may not be certified.
q | Direct any questions about this specification or the process to SITA at tas@sita.co.za or (012) 482 2870.
q | All rights and intellectual property herein are vested with SITA. No part of the contents of this document may be used, copied, disclosed or conveyed in whole or in part to any party in any manner whatsoever, other than for the purpose of preparing a proposal in response to this specification, without written permission from SITA.
Definitions
Definitions and acronyms are typically based on industry-standard terms, but in case of deviation shall have the
meaning assigned to them within this specification or the wider TCP.
q | Installation charge: the price charged by the OEM's partner to install the product in the client environment. This includes unpacking, connecting cables, power-up and user acceptance. May be required as part of the base solution price, depending on category.
q | OEM: Original Equipment Manufacturer, or properly delegated legal entity representing a product brand in South Africa.
q | Repair: any action taken by the OEM or service partner to ensure that a working solution is available to the client within the specified turnaround time. This can include physically repairing the system on-site, or swopping out the system or a faulty component.
q | Service Delivery Zones: Geographical areas within South Africa where product and service delivery are required. These areas are designated as Zone A, B or C, depending on proximity to large centres. The zones are defined as follows, along with the required baseline business-hours SLA:
Zone A - 4-hour response, repair within next business day: The entire Gauteng Province, as well as in or within 50km from major cities or Provincial capitals, i.e. Cape Town, Gqeberha, Buffalo City, Bisho, Bloemfontein, Durban, Mmabatho, Polokwane, Kimberley, Pietermaritzburg, Ulundi, eMalahleni and Mbombela. Zone B - 4-hour response, repair within 2 business days: In or within 50km from major towns, i.e. Naledi (Welkom), Umtata, George, Makhanda, Thohoyandou, Madibeng, Klerksdorp, Ermelo, Standerton, Ladysmith, Oudtshoorn, Richards Bay, Saldanha, Upington, Worcester, Potchefstroom and Beaufort West. Zone C - 4-hour response, repair within 3 business days: All towns and rural areas not included in Zone A and Zone B where services may be required.
q | "Support for": a capability that a product must enable, but must not necessarily have built-in or included in the solution price without an optional accessory or upgrade.
q | Warranty and Support: As per detail technical specifications, unless indicated otherwise, the following standard warranty and SLA must be included with all supplied solutions and products:
Countrywide on-site with full coverage (parts and labour for entire Item, upgrades and accessories) during office hours (7:30 - 17:00), with next business-day repair (Zone-dependent as per definitions) for 5 years (60 months) from date of delivery.
Technical Specification Form
q | The Technical Specifications/Pricing Schedule and other applicable forms must be completed electronically and submitted along with the rest of the mandatory documentation. The completed specification must be submitted as a .XLSX file incorporating all products and derivatives, mandatory technical answers and OEM ceiling prices.
q | Sections 1 and 2 on the technical Item documents are mandatory: all information in these sections must be complied with and completed in full. Section 2 also contains additional price lines where OEMs may supply pricing for additional components. Only components that are directly related to the offered system may be added in Section 2.
q | All features, capabilities, options, accessories, software, drivers, warranties, cables, etc. listed under "Standard Components" (Paragraph B) must be included in the Solution Price. Products without all required components and functionality will not be certified.
q | Lines in the specification that have the word "preferred" are non-mandatory specs, i.e. a "No" answer is acceptable. A "Yes" answer indicates that the option/feature is included in the Solution Price.
q | If an OEM product family includes multiple devices that comply fully with the specified requirements, multiple products may be submitted as derivatives under a single submission (priced separately). Multiple submissions may be made for different families of products.
q | A 5-10% deviation will be allowed on certain mandatory numerical specifications, e.g. noise levels (dBA), unit weights and size, battery life and performance figures. Products that fall within this range in terms of technical specifications may be accepted, despite being below spec. SITA reserves the right to make the final decision in any such matters.
● Noise levels higher than the specified value will be accepted on a sliding scale based on increased device performance or configuration.
q | This .xlsx-based specification document may not be changed in any way, including changing specification details, line numbers, or adding or removing lines or columns. To prevent this, the document is locked and protected. Submissions that do not correspond 100% to the original layout and content (including draft versions of the spec that were circulated earlier) will not be certified.
q | All worksheet cells in the spec are locked and password protected, except where input is required. Input fields are clearly visible in the form, with bold underlined formatting, with a light red fill for mandatory fields. Calculations may be performed on some worksheets. Data validation is performed on all fields. Illegal entries will not be accepted.
q | Pricing represents OEM ceiling prices only, and are solely for use as an indicative calculation of total cost of ownership. It is not a quote, will not be used for negotiation, and will not be used in any tender. All prices must include VAT.
q | Prices for non-mandatory components or options (R0.00 by default) may not exceed R500 000 per line.
q | The "Comments/Details/Model #" field is reserved for model numbers and/or product details or comments. This information must be entered for all components and accessories. Any additional notes on the answer may also be entered here, e.g. "See Appendix" or "Included as standard". Note: The comments field may not be used to modify the answer or avoid the question.
q | Lines in the specification beginning with "State" require OEMs to supply important information on the submitted product. These lines must be completed as required. Keep "State" answers as short as possible, providing only pertinent technical information without lengthy explanations. Reference may be made to external documentation for more extensive answers.
q | For purposes of the Technical evaluation, "N/A" is defined as "Not Applicable". A comment on a mandatory specification indicating "Not Available" or "Not Applicable" may result in non-certification of the submission.
q | Empty answers may lead to non-certification of the submission.

## Profiles
Technology Certification: Item Profiles
Infrastructure Solutions (TU2, v2.0, H2 2024)
Note: This specification is subject to change based on Government requirements, and is reviewed periodically via a
Tech Update (TU) process.
The table below serves as a high-level overview of what is required per category, and will not be used for evaluation.
Products will be evaluated against the detail specs in the individual Item sheets, which must be completed.
Changes from the previous version are marked in BLUE on this sheet and the detail spec sheets below.
Uninterruptible Power Supplies (UPS)
Single-phase UPS
Item | Title | Description
UPS_Li1 | Entry-level line-interactive UPS | Entry-level single-phase line-interactive uninterruptible power supply
UPS_Li2 | Midrange line-interactive UPS | Midrange single-phase line-interactive uninterruptible power supply
UPS_OL1 | Entry-level on-line UPS | Entry-level single-phase online (double-conversion) uninterruptible power supply
UPS_OL2 | Midrange on-line UPS | Midrange single-phase online (double-conversion) uninterruptible power supply
UPS_OL3 | Advanced on-line UPS | Advanced single-phase online (double-conversion) uninterruptible power supply
3-phase UPS
Item | Title | Description
UPS_OL4 | Advanced 3-phase on-line UPS | Advanced three-phase online (double-conversion) uninterruptible power supply
UPS_OL5 | 3-phase building UPS | Three-phase online (double-conversion) uninterruptible power supply for building backup power supply
UPS_OL6 | 3-phase datacentre UPS | Three-phase online (double-conversion) uninterruptible power supply for datacentre backup power supply
Equipment Racks
Item | Title | Description
Rack_Wb | Wall-mount cabinet | Wall-mount communications/network equipment cabinet (wallbox)
Rack_Net | Network Cabinet | Stand-alone 19" equipment cabinet, optimised for networking devices and cabling
Rack_Srv | Server Rack | Stand-alone 19" equipment cabinet, optimised for server and storage systems
Rack_Env | Environmental Rack | Stand-alone 19" equipment rack with environmental controls, optimised for deployment in uncontrolled environments
Rack_AV | Audiovisual Rack | Stand-alone 19" equipment cabinet, optimised for audiovisual applications, incl. with boardroom integration options
System Management and Monitoring
Item | Title | Description
Env_Mon | Environmental monitoring | Environmental monitoring and control solution including sensors, devices and connectivity to enable remote monitoring, management and security of data center environments
Infra_Mgmt | Infrastructure management tools | System and infrastructure management and monitoring tools/software, providing alerts, configuration, deployment support and remote control to enable cost and labour reduction and/or value-added services for data and switching centre solutions
Supporting Components and Services
Alternative Power Infrastructure
Item | Title | Description
BESS1 | Entry-level BESS solution | Basic power backup and energy storage solution, including inverter and batteries, with optional solar generation using PV panels. Designed, installed and maintained according to Government electrical standards
BESS2 | Midrange BESS solution | Midrange power backup and energy storage solution, including inverter and batteries, with optional solar generation using PV panels. Designed, installed and maintained according to Government electrical standards
BESS3 | Advanced BESS solution | Advanced power backup and energy storage solution, including inverter and batteries, with optional solar generation using PV panels. Designed, installed and maintained according to Government electrical standards
Gen1 | Entry-level generator solution | Basic diesel generator solution. Designed, installed and maintained according to published Government electrical standards
Gen2 | Midrange generator solution | Midrange diesel generator solution. Designed, installed and maintained according to published Government electrical standards
Gen3 | Advanced generator solution | Advanced diesel generator solution. Designed, installed and maintained according to published Government electrical standards
IT Facility Infrastructure
Item | Title | Description
Cabling | Ducting, trenching, routing | Complete IT facility infrastructure solutions, including cable routing, raised flooring, cooling, power and fire supression. Designed, installed and maintained according to published Government building infrastructure and safety standards
Flooring | Raised flooring system
HVAC | Cooling
Power | Power distribution
Fire | Fire suppression
Services: Bundled + Ad Hoc
Item/Profile |  | Description
Needs analysis |  | ● All services to be quoted and supplied as required by project needs. ● Basic services such as delivery, installation and support must be bundled with ALL solutions, as per the Detail Specification. ● The standard 5-year SLA can be upgraded further at the client's discretion. ● Specialised or ad hoc services will be specified in the client RFP/RFQ, and must be fully catered for by the proposed solution. ● All required travelling and accommodation (S&T) must be included in the quoted total solution cost.
Design
Consultation
Supply and Delivery
Installation and configuration
Integration
Commissioning
Familiarisation and Training
Operations
System management
Support and Maintenance
On-site tech resource
End-of-life services
Glossary/Acronyms
BESS | Battery Energy Storage Solution
EMC | Electromagnetic Compatibility
ESM | Enterprise System Management
HVAC | Heating, Ventilation and Air Conditioning
IPxy | Standard for solid & liquid ingress protection (IEC 60529)
IPvX | Internet Protocol version (e.g. IPv6)
LiFEPO4 | Lithium Iron Phosphate (LFP) - advanced battery chemistry offering better performance at higher cost
MoA | Memorandum of Agreement
MTBF | Mean Time Before Failure
MTTR | Mean Time To Repair
NIC | Network Interface Card
PV | Photovoltaic technology used in solar panels
RFP/Q/B | Request for Proposal/Quotation/Bid
SLA | Service Level Agreement
SNMP | Simple Network Management Protocol
SMTP | Simple Mail Transfer Protocol
THDi | Total Harmonic Distortion (current)
UPS | Uninterruptible Power Supply
USB | Universal Serial Bus
Categories: | 7
Items: | 30
Date: | 2024-10-02 16:20

## UPS_Li1
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
UPS_Li1: Entry-level line-interactive UPS
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Entry-level single-phase line-interactive uninterruptible power supply | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Output capacity: 1 KVA (UPS must be sized to meet the specified wattage) | No
A.4 | Effective load-bearing capacity: 800W with at least 80% efficiency | No
A.5 | Runtime: at power loss, the UPS must maintain power to the full load for at least 5 minutes | No
A.5a) | The UPS must notify attached systems of power failure to allow graceful shutdown | No
A.6 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.7 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Software included with system:
B.2a) | Client software for latest versions of operating systems as specified | No
B.2b) | Installation and configuration tools | No
B.2c) | Diagnostic and management tools | No
B.3 | Power cables: input and output as required | No
B.4 | Host communications cable (RS-232 or USB) | No
B.5 | Mounting rails (only for rack-mount solutions) | No
B.6 | Services included:
B.6a) | On-site installation and configuration | No
B.6b) | End-user training of at least 30 minutes | No
C. | System Properties and Functionality
C.1 | UPS capabilities:
C.1a) | Single-phase design for input and output | No
C.1b) | State UPS load-bearing rating: Watts
C.1c) | State UPS load-bearing rating: KVA
C.1d) | State runtime at full load for base system (minutes)
C.1e) | Support for extended runtime via battery upgrades preferred | No
C.1f) | State derating coefficient (altitude, temperature, etc.)
C.2 | Runtime:
C.2a) | State baseline runtime support @ 50% load (minutes)
C.2b) | State baseline runtime support @ 100% load (minutes)
C.2c) | State maximum runtime supported with all possible runtime upgrades @ 50% load (minutes)
C.2d) | State maximum runtime supported with all possible runtime upgrades @ 100% load (minutes)
C.3 | Battery functionality and management:
C.3a) | Replaceable batteries | No
C.3b) | Integrated battery test and protection mechanisms | No
C.3c) | Battery replacement indicator | No
C.3d) | Charger capacity: batteries must be recharged to 90% capacity in 4 hours | No
C.4 | Outputs:
C.4a) | IEC 60320 output ports: at least 4x type C13 (10A) | No
C.4b) | Software-controlled outputs preferred | No
C.5 | Output waveform: pure sine wave | No
D. | Availability and Reliability
D.1 | Batteries are excluded from the standard equipment warranty, but must be covered by the same warranty conditions for a 2-year period | No
D.1a) | State warranty terms for batteries
D.1b) | State the period for which the batteries are guaranteed unconditionally
D.2 | State MTBF (mean time before failure) for base system (power-on hours)
E. | System Management
E.1 | Integrated remote management, configuration and monitoring functionality preferred | No
E.1a) | Failure alerts and status warnings via SNMP, SMTP or other mechanism preferred | No
E.1b) | Web standards-based remote management preferred | No
E.1c) | Remote power cycling of individual output ports preferred | No
E.2 | Remote monitoring and alerts:
E.2a) | Status and performance metrics preferred | No
E.2b) | Power status on individual output ports preferred | No
E.2c) | Battery status/failures preferred | No
E.2d) | Component failures preferred | No
E.3 | Support for integration into enterprise-level management suites (e.g. OpenView, SCCM, Tivoli, UniCentre) preferred | No
E.4 | Integrated control panel for information, configuration and administration preferred | No
E.5 | Connectivity:
E.5a) | USB or RS-232 interface | No
E.5b) | 10/100BT Ethernet port preferred | No
E.6 | Device drivers and software:
E.6a) | Software can be downloaded from a generally-available Web site | No
E.6b) | Software for previous versions of supported OSes must be made available on request | No
E.7 | Firmware updates must be made available free of charge for the entire warranty period | No
E.8 | Documentation for complete solution with configuration and operation guidelines | No
E.9 | System model change lifecycle: at least 12 months from introduction to replacement | No
F. | System enclosure and Environmental Characteristics
F.1 | System form factor: rack-mount or tower | No
F.1a) | Form factor is convertible preferred | No
F.1b) | State enclosure size in rack units (u)
F.2 | Power and cooling characteristics:
F.2a) | Power supply: 220/230 VAC ±10%, 50 Hz | No
F.2b) | Tolerance for voltage and frequency fluctuations: UPS must support a sustained 50% load without switching to batteries within 160-270VAC and 50Hz ±2% (acceptable derating at lower voltages will be allowed) | No
F.2c) | IEC 60320 power connectors | No
F.2d) | State maximum power consumption (Watts) for UPS (i.e. while charging batteries at full load) | 9999
F.2e) | State maximum cooling requirements (BTU/hour) for UPS (i.e. while charging batteries at full load) | 9999
F.3 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
G. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
G.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
G.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
G.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
G.3 | Only components that are supported by the OEM may be bundled with the solution | No
G.4 | Operating system support:
G.4a) | Microsoft Windows Server: current and previous version | No
G.4b) | Linux: at least 1 major enterprise distro (Specify distros that the system is certified for in Comments column) | No
G.4c) | Solaris, BSD or other Unix preferred | No
G.4d) | Mainstream hypervisors, incl. VMware, Hyper-V and KVM preferred | No
G.5 | High-level diagram of system architecture (showing interfaces and major components) must be included with submission | No
G.6 | UPS efficiency graph must be included with submission | No
G.7 | Manufacturing certifications:
G.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
G.7b) | ISO 14001: certification for environmental management | No
G.7c) | Reduction of Hazardous Substances (RoHS) | No
G.7d) | State country of manufacture
G.8 | UPS standards compliance (international certification acceptable):
G.8a) | IEC/EN 62040-1: UPS safety requirements | No
G.8b) | IEC/EN 62040-2: UPS EMC requirements | No
G.8c) | IEC/EN 62040-3: UPS efficiency preferred | No
G.8d) | IEC/EN 62040-4: UPS environmental aspects preferred | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
H. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
H.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
H.1a) | Base product _________________________________ | 999999.99
H.1b) | Derivative 1 __________________________________ | 0
H.1c) | Derivative 2 __________________________________ | 0
H.1d) | Derivative 3 __________________________________ | 0
H.1e) | Derivative 4 __________________________________ | 0
H.1f) | Derivative 5 __________________________________ | 0
I. | Services
I.1 | Warranty extensions:
I.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
I.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1d) | Additional SLA/service option ____________________ | 0
I.1e) | Additional SLA/service option ____________________ | 0
I.1f) | Additional SLA/service option ____________________ | 0
I.1g) | Additional SLA/service option ____________________ | 0
I.2 | Installation charge for base eval config | 999999.99
I.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
I.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
J. | Additional Components
J.1 | Extended runtime modules:
J.1a) | Runtime module _______________________________ | 0
J.1b) | Runtime module _______________________________ | 0
J.2 | Replacement batteries:
J.2a) | Battery module _______________________________ | 0
J.2b) | Battery module _______________________________ | 0
J.2c) | Battery module _______________________________ | 0
J.2d) | Battery module _______________________________ | 0
J.3 | Power cables:
J.3a) | Power cable _________________________________ | 0
J.3b) | Power cable _________________________________ | 0
J.3c) | Power cable _________________________________ | 0
J.3d) | Power cable _________________________________ | 0
J.4 | Remote management:
J.4a) | SNMP module | 0
J.4b) | Other management module ______________________ | 0
J.4c) | Other management module ______________________ | 0
J.4d) | Other management module ______________________ | 0
J.5 | Software:
J.5a) | Software option _______________________________ | 0
J.5b) | Software option _______________________________ | 0
J.5c) | Software option _______________________________ | 0
J.5d) | Software option _______________________________ | 0
J.6 | Rack-mount rails and tower conversion kit | 0
J.7 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
J.7a) | Additional component __________________________ | 0
J.7b) | Additional component __________________________ | 0
J.7c) | Additional component __________________________ | 0
J.7d) | Additional component __________________________ | 0
J.7e) | Additional component __________________________ | 0
J.7f) | Additional component __________________________ | 0
J.7g) | Additional component __________________________ | 0
J.7h) | Additional component __________________________ | 0
J.7i) | Additional component __________________________ | 0
J.7j) | Additional component __________________________ | 0
J.7k) | Additional component __________________________ | 0
J.7l) | Additional component __________________________ | 0
J.7m) | Additional component __________________________ | 0
J.7n) | Additional component __________________________ | 0
J.7o) | Additional component __________________________ | 0
J.7p) | Additional component __________________________ | 0
J.7q) | Additional component __________________________ | 0
J.7r) | Additional component __________________________ | 0
J.7s) | Additional component __________________________ | 0
J.7t) | Additional component __________________________ | 0

## UPS_Li2
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
UPS_Li2: Midrange line-interactive UPS
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Midrange single-phase line-interactive uninterruptible power supply | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Output capacity: 2 KVA (UPS must be sized to meet the specified wattage) | No
A.4 | Effective load-bearing capacity: 1600W with at least 80% efficiency | No
A.5 | Runtime: at power loss, the UPS must maintain power to the full load for at least 5 minutes | No
A.5a) | The UPS must notify attached systems of power failure to allow graceful shutdown | No
A.6 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.7 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Software included with system:
B.2a) | Client software for latest versions of operating systems as specified | No
B.2b) | Installation and configuration tools | No
B.2c) | Diagnostic and management tools | No
B.3 | Power cables: input and output as required | No
B.4 | Mounting rails (only for rack-mount solutions) | No
B.5 | Services included:
B.5a) | On-site installation and configuration | No
B.5b) | End-user training of at least 30 minutes | No
C. | System Properties and Functionality
C.1 | UPS capabilities:
C.1a) | Single-phase design for input and output | No
C.1b) | State UPS load-bearing rating: Watts
C.1c) | State UPS load-bearing rating: KVA
C.1d) | State runtime at full load for base system (minutes)
C.1e) | Support for extended runtime via battery upgrades preferred | No
C.1f) | State derating coefficient (altitude, temperature, etc.)
C.2 | Runtime:
C.2a) | State baseline runtime support @ 50% load (minutes)
C.2b) | State baseline runtime support @ 100% load (minutes)
C.2c) | State maximum runtime supported with all possible runtime upgrades @ 50% load (minutes)
C.2d) | State maximum runtime supported with all possible runtime upgrades @ 100% load (minutes)
C.3 | Battery functionality and management:
C.3a) | Replaceable batteries | No
C.3b) | Integrated battery test and protection mechanisms | No
C.3c) | Battery replacement indicator | No
C.3d) | Charger capacity: batteries must be recharged to 90% capacity in 6 hours | No
C.4 | Outputs:
C.4a) | IEC 60320 output ports: at least 6x type C13 and 1x C19 (10A/16A) | No
C.4b) | Software-controlled outputs | No
C.5 | Output waveform: pure sine wave | No
D. | Availability and Reliability
D.1 | Batteries are excluded from the standard equipment warranty, but must be covered by the same warranty conditions for a 2-year period | No
D.1a) | State warranty terms for batteries
D.1b) | State the period for which the batteries are guaranteed unconditionally
D.2 | State MTBF (mean time before failure) for base system (power-on hours)
E. | System Management
E.1 | Integrated remote management, configuration and monitoring functionality preferred | No
E.1a) | Failure alerts and status warnings via SNMP, SMTP or other mechanism preferred | No
E.1b) | Web standards-based remote management | No
E.1c) | Remote power cycling of individual output ports preferred | No
E.2 | Remote monitoring and alerts:
E.2a) | Status and performance metrics | No
E.2b) | Power status on individual output ports preferred | No
E.2c) | Battery status/failures | No
E.2d) | Component failures | No
E.3 | Support for integration into enterprise-level management suites (e.g. OpenView, SCCM, Tivoli, UniCentre) | No
E.4 | Integrated control panel for information, configuration and administration | No
E.5 | Connectivity:
E.5a) | USB or RS-232 interface | No
E.5b) | 10/100BT Ethernet port preferred | No
E.6 | Security:
E.6a) | Role- or ACL-based management access control (e.g. Operator / Supervisor) preferred | No
E.6b) | Support for industry-standard, secure protocols (e.g. SSH, HTTPS, SSL/TLS) preferred | No
E.6c) | Firmware and software updates digitally signed by OEM to mimise risk of updates preferred | No
E.6d) | Communications security verified by third party preferred | No
E.6e) | Support for IEC 62443-4-2 and UL 2900-1 cybersecurity standards preferred | No
E.7 | Device drivers and software:
E.7a) | Software can be downloaded from a generally-available Web site | No
E.7b) | Software for previous versions of supported OSes must be made available on request | No
E.8 | Firmware updates must be made available free of charge for the entire warranty period | No
E.9 | Documentation for complete solution with configuration and operation guidelines | No
E.10 | System model change lifecycle: at least 12 months from introduction to replacement | No
F. | System enclosure and Environmental Characteristics
F.1 | System form factor: rack-mount or tower | No
F.1a) | Form factor is convertible preferred | No
F.1b) | State enclosure size in rack units (u)
F.2 | Power and cooling characteristics:
F.2a) | Power supply: 220/230 VAC ±10%, 50 Hz | No
F.2b) | Tolerance for voltage and frequency fluctuations: UPS must support a sustained 50% load without switching to batteries within 160-270VAC and 50Hz ±2% (acceptable derating at lower voltages will be allowed) | No
F.2c) | IEC 60320 power connectors | No
F.2d) | State maximum power consumption (Watts) for UPS (i.e. while charging batteries at full load) | 9999
F.2e) | State maximum cooling requirements (BTU/hour) for UPS (i.e. while charging batteries at full load) | 9999
F.3 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
G. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
G.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
G.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
G.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
G.3 | Only components that are supported by the OEM may be bundled with the solution | No
G.4 | Operating system support:
G.4a) | Microsoft Windows Server: current and previous version | No
G.4b) | Linux: at least 1 major enterprise distro (Specify distros that the system is certified for in Comments column) | No
G.4c) | Solaris, BSD or other Unix preferred | No
G.4d) | Mainstream hypervisors, incl. VMware, Hyper-V and KVM preferred | No
G.5 | High-level diagram of system architecture (showing interfaces and major components) must be included with submission | No
G.6 | UPS efficiency graph must be included with submission | No
G.7 | Manufacturing certifications:
G.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
G.7b) | ISO 14001: certification for environmental management | No
G.7c) | Reduction of Hazardous Substances (RoHS) | No
G.7d) | State country of manufacture
G.8 | UPS standards compliance (international certification acceptable):
G.8a) | IEC/EN 62040-1: UPS safety requirements | No
G.8b) | IEC/EN 62040-2: UPS EMC requirements | No
G.8c) | IEC/EN 62040-3: UPS efficiency preferred | No
G.8d) | IEC/EN 62040-4: UPS environmental aspects preferred | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
H. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
H.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
H.1a) | Base product _________________________________ | 999999.99
H.1b) | Derivative 1 __________________________________ | 0
H.1c) | Derivative 2 __________________________________ | 0
H.1d) | Derivative 3 __________________________________ | 0
H.1e) | Derivative 4 __________________________________ | 0
H.1f) | Derivative 5 __________________________________ | 0
I. | Services
I.1 | Warranty extensions:
I.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
I.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1d) | Additional SLA/service option ____________________ | 0
I.1e) | Additional SLA/service option ____________________ | 0
I.1f) | Additional SLA/service option ____________________ | 0
I.1g) | Additional SLA/service option ____________________ | 0
I.2 | Installation charge for base eval config | 999999.99
I.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
I.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
J. | Additional Components
J.1 | Extended runtime modules:
J.1a) | Runtime module _______________________________ | 0
J.1b) | Runtime module _______________________________ | 0
J.1c) | Runtime module _______________________________ | 0
J.1d) | Runtime module _______________________________ | 0
J.2 | Replacement batteries:
J.2a) | Battery module _______________________________ | 0
J.2b) | Battery module _______________________________ | 0
J.2c) | Battery module _______________________________ | 0
J.3 | Battery module _______________________________ | 0
J.4 | Power Distribution Units:
J.4a) | PDU: 8 IEC 60320 outputs | 0
J.4b) | PDU _______________________________________ | 0
J.4c) | PDU _______________________________________ | 0
J.4d) | PDU _______________________________________ | 0
J.5 | Power cables:
J.5a) | Power cable _________________________________ | 0
J.5b) | Power cable _________________________________ | 0
J.5c) | Power cable _________________________________ | 0
J.5d) | Power cable _________________________________ | 0
J.6 | Remote management:
J.6a) | SNMP module | 0
J.6b) | Other management module ______________________ | 0
J.6c) | Other management module ______________________ | 0
J.6d) | Other management module ______________________ | 0
J.7 | Software:
J.7a) | Software option _______________________________ | 0
J.7b) | Software option _______________________________ | 0
J.7c) | Software option _______________________________ | 0
J.7d) | Software option _______________________________ | 0
J.8 | Rack-mount rails and tower conversion kit | 0
J.9 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
J.9a) | Additional component __________________________ | 0
J.9b) | Additional component __________________________ | 0
J.9c) | Additional component __________________________ | 0
J.9d) | Additional component __________________________ | 0
J.9e) | Additional component __________________________ | 0
J.9f) | Additional component __________________________ | 0
J.9g) | Additional component __________________________ | 0
J.9h) | Additional component __________________________ | 0
J.9i) | Additional component __________________________ | 0
J.9j) | Additional component __________________________ | 0
J.9k) | Additional component __________________________ | 0
J.9l) | Additional component __________________________ | 0
J.9m) | Additional component __________________________ | 0
J.9n) | Additional component __________________________ | 0
J.9o) | Additional component __________________________ | 0
J.9p) | Additional component __________________________ | 0
J.9q) | Additional component __________________________ | 0
J.9r) | Additional component __________________________ | 0
J.9s) | Additional component __________________________ | 0
J.9t) | Additional component __________________________ | 0

## UPS_OL1
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
UPS_OL1: Entry-level on-line UPS
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Entry-level single-phase online (double-conversion) uninterruptible power supply | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Output capacity: 1 KVA (UPS must be sized to meet the specified wattage) | No
A.4 | Effective load-bearing capacity: 900W with at least 90% efficiency | No
A.5 | Runtime: at power loss, the UPS must maintain power to the full load for at least 5 minutes | No
A.5a) | The UPS must notify attached systems of power failure to allow graceful shutdown | No
A.5b) | Battery must be sized based on client's runtime requirement, if greater than 5 minutes | No
A.6 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.7 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Software included with system:
B.2a) | Client software for latest versions of operating systems as specified | No
B.2b) | Installation and configuration tools | No
B.2c) | Diagnostic and management tools | No
B.3 | Power cables: input and output as required | No
B.4 | Host communications cable (RS-232 or USB) | No
B.5 | Mounting rails (only for rack-mount solutions) | No
B.6 | Services included:
B.6a) | On-site installation and configuration | No
B.6b) | End-user training of at least 1 hour | No
C. | System Properties and Functionality
C.1 | UPS capabilities:
C.1a) | Single-phase design for input and output | No
C.1b) | State UPS load-bearing rating: Watts
C.1c) | State UPS load-bearing rating: KVA
C.1d) | State runtime at full load for base system (minutes)
C.1e) | Support for extended runtime via battery upgrades preferred | No
C.1f) | State derating coefficient (altitude, temperature, etc.)
C.2 | Runtime:
C.2a) | State baseline runtime support @ 50% load (minutes)
C.2b) | State baseline runtime support @ 100% load (minutes)
C.2c) | State maximum runtime supported with all possible runtime upgrades @ 50% load (minutes)
C.2d) | State maximum runtime supported with all possible runtime upgrades @ 100% load (minutes)
C.2e) | Support for high-efficiency/eco mode (>95%) | No
C.2f) | Generator support: THDi < 5% | No
C.2g) | Ability to function and provide clean power while battery is discharged or being serviced | No
C.2h) | Hypervisor support: ability to integrate into virtualisation management and shut down or migrate virtual servers when power is lost preferred | No
C.3 | Battery functionality and management:
C.3a) | Hot-swappable batteries preferred | No
C.3b) | Integrated battery test and protection mechanisms | No
C.3c) | Battery replacement indicator | No
C.3d) | Charger capacity: batteries must be recharged to 90% capacity in 4 hours | No
C.3e) | Support for optional lithium-based batteries preferred | No
C.4 | Outputs:
C.4a) | IEC 60320 output ports: at least 4x type C13 (10A) | No
C.4b) | Software-controlled outputs preferred | No
C.5 | Output waveform: pure sine wave | No
D. | Availability and Reliability
D.1 | Batteries are excluded from the standard equipment warranty, but must be covered by the same warranty conditions for a 2-year period | No
D.1a) | State warranty terms for batteries
D.1b) | State the period for which the batteries are guaranteed unconditionally
D.2 | State MTBF (mean time before failure) for base system (power-on hours)
E. | System Management
E.1 | Integrated remote management, configuration and monitoring functionality preferred | No
E.1a) | Failure alerts and status warnings via SNMP, SMTP or other mechanism preferred | No
E.1b) | Web standards-based remote management preferred | No
E.1c) | Remote power cycling of individual output ports preferred | No
E.2 | Remote monitoring and alerts:
E.2a) | Status and performance metrics | No
E.2b) | Power status on individual output ports preferred | No
E.2c) | Battery status/failures | No
E.2d) | Component failures | No
E.3 | Support for integration into enterprise-level management suites (e.g. OpenView, SCCM, Tivoli, UniCentre) preferred | No
E.4 | Integrated control panel for information, configuration and administration | No
E.5 | Connectivity:
E.5a) | USB or RS-232 interface | No
E.5b) | 10/100BT Ethernet port preferred | No
E.6 | Device drivers and software:
E.6a) | Software can be downloaded from a generally-available Web site | No
E.6b) | Software for previous versions of supported OSes must be made available on request | No
E.7 | Firmware updates must be made available free of charge for the entire warranty period | No
E.8 | Documentation for complete solution with configuration and operation guidelines | No
E.9 | System model change lifecycle: at least 12 months from introduction to replacement | No
F. | System enclosure and Environmental Characteristics
F.1 | System form factor: rack-mount or tower | No
F.1a) | Form factor is convertible preferred | No
F.1b) | State enclosure size in rack units (u)
F.2 | Power and cooling characteristics:
F.2a) | Power supply: 220/230 VAC ±10%, 50 Hz | No
F.2b) | Tolerance for voltage and frequency fluctuations: UPS must support a sustained 50% load without switching to batteries within 120-270VAC and 50Hz ±15% (acceptable derating at lower voltages will be allowed) | No
F.2c) | IEC 60320 power connectors | No
F.2d) | State maximum power consumption (Watts) for UPS (i.e. while charging batteries at full load) | 9999
F.2e) | State maximum cooling requirements (BTU/hour) for UPS (i.e. while charging batteries at full load) | 9999
F.3 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
G. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
G.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
G.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
G.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
G.3 | Only components that are supported by the OEM may be bundled with the solution | No
G.4 | Operating system support:
G.4a) | Microsoft Windows Server: current and previous version | No
G.4b) | Linux: at least 1 major enterprise distro (Specify distros that the system is certified for in Comments column) | No
G.4c) | Solaris, BSD or other Unix preferred | No
G.4d) | Mainstream hypervisors, incl. VMware, Hyper-V and KVM preferred | No
G.5 | High-level diagram of system architecture (showing interfaces and major components) must be included with submission | No
G.6 | UPS efficiency graph must be included with submission | No
G.7 | Manufacturing certifications:
G.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
G.7b) | ISO 14001: certification for environmental management | No
G.7c) | Reduction of Hazardous Substances (RoHS) | No
G.7d) | State country of manufacture
G.8 | UPS standards compliance (international certification acceptable):
G.8a) | IEC/EN 62040-1: UPS safety requirements | No
G.8b) | IEC/EN 62040-2: UPS EMC requirements | No
G.8c) | IEC/EN 62040-3: UPS efficiency preferred | No
G.8d) | IEC/EN 62040-4: UPS environmental aspects preferred | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
H. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
H.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
H.1a) | Base product _________________________________ | 999999.99
H.1b) | Derivative 1 __________________________________ | 0
H.1c) | Derivative 2 __________________________________ | 0
H.1d) | Derivative 3 __________________________________ | 0
H.1e) | Derivative 4 __________________________________ | 0
H.1f) | Derivative 5 __________________________________ | 0
I. | Services
I.1 | Warranty extensions:
I.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
I.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1d) | Additional SLA/service option ____________________ | 0
I.1e) | Additional SLA/service option ____________________ | 0
I.1f) | Additional SLA/service option ____________________ | 0
I.1g) | Additional SLA/service option ____________________ | 0
I.2 | Installation charge for base eval config | 999999.99
I.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
I.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
J. | Additional Components
J.1 | Extended runtime modules:
J.1a) | Runtime module _______________________________ | 0
J.1b) | Runtime module _______________________________ | 0
J.2 | Replacement batteries:
J.2a) | Battery module _______________________________ | 0
J.2b) | Battery module _______________________________ | 0
J.2c) | Battery module _______________________________ | 0
J.2d) | Battery module _______________________________ | 0
J.3 | Power cables:
J.3a) | Power cable _________________________________ | 0
J.3b) | Power cable _________________________________ | 0
J.3c) | Power cable _________________________________ | 0
J.3d) | Power cable _________________________________ | 0
J.4 | Remote management:
J.4a) | SNMP module | 0
J.4b) | Other management module ______________________ | 0
J.4c) | Other management module ______________________ | 0
J.4d) | Other management module ______________________ | 0
J.5 | Software:
J.5a) | Software option _______________________________ | 0
J.5b) | Software option _______________________________ | 0
J.5c) | Software option _______________________________ | 0
J.5d) | Software option _______________________________ | 0
J.6 | Rack-mount rails and tower conversion kit | 0
J.7 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
J.7a) | Additional component __________________________ | 0
J.7b) | Additional component __________________________ | 0
J.7c) | Additional component __________________________ | 0
J.7d) | Additional component __________________________ | 0
J.7e) | Additional component __________________________ | 0
J.7f) | Additional component __________________________ | 0
J.7g) | Additional component __________________________ | 0
J.7h) | Additional component __________________________ | 0
J.7i) | Additional component __________________________ | 0
J.7j) | Additional component __________________________ | 0
J.7k) | Additional component __________________________ | 0
J.7l) | Additional component __________________________ | 0
J.7m) | Additional component __________________________ | 0
J.7n) | Additional component __________________________ | 0
J.7o) | Additional component __________________________ | 0
J.7p) | Additional component __________________________ | 0
J.7q) | Additional component __________________________ | 0
J.7r) | Additional component __________________________ | 0
J.7s) | Additional component __________________________ | 0
J.7t) | Additional component __________________________ | 0

## UPS_OL2
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
UPS_OL2: Midrange on-line UPS
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Midrange single-phase online (double-conversion) uninterruptible power supply | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Output capacity: 3 KVA (UPS must be sized to meet the specified wattage) | No
A.4 | Effective load-bearing capacity: 2700W with at least 90% efficiency | No
A.5 | Runtime: at power loss, the UPS must maintain power to the full load for at least 5 minutes | No
A.5a) | The UPS must notify attached systems of power failure to allow graceful shutdown | No
A.5b) | Battery must be sized based on client's runtime requirement, if greater than 5 minutes | No
A.6 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.7 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Software included with system:
B.2a) | Client software for latest versions of operating systems as specified | No
B.2b) | Network shutdown software | No
B.2c) | Installation and configuration tools | No
B.2d) | Diagnostic and management tools | No
B.3 | Network management module (SNMP or equivalent) | No
B.4 | Power cables: input and output as required | No
B.5 | Mounting rails (only for rack-mount solutions) | No
B.6 | Services included:
B.6a) | On-site installation and configuration | No
B.6b) | End-user training of at least 1 hour | No
C. | System Properties and Functionality
C.1 | UPS capabilities:
C.1a) | Single-phase design for input and output | No
C.1b) | State UPS load-bearing rating: Watts
C.1c) | State UPS load-bearing rating: KVA
C.1d) | State runtime at full load for base system (minutes)
C.1e) | Support for extended runtime via battery upgrades | No
C.1f) | State derating coefficient (altitude, temperature, etc.)
C.2 | Runtime:
C.2a) | State baseline runtime support @ 50% load (minutes)
C.2b) | State baseline runtime support @ 100% load (minutes)
C.2c) | State maximum runtime supported with all possible runtime upgrades @ 50% load (minutes)
C.2d) | State maximum runtime supported with all possible runtime upgrades @ 100% load (minutes)
C.2e) | Ability to function and provide clean power while battery is discharged or being serviced | No
C.2f) | Support for high-efficiency/eco mode (>95%) | No
C.2g) | Generator support: THDi < 5% | No
C.2h) | Hypervisor support: ability to integrate into virtualisation management and shut down or migrate virtual servers when power is lost | No
C.3 | Battery functionality and management:
C.3a) | Hot-swappable batteries preferred | No
C.3b) | Integrated battery test and protection mechanisms | No
C.3c) | Battery replacement indicator | No
C.3d) | Charger capacity: batteries must be recharged to 90% capacity in 6 hours | No
C.3e) | Support for optional lithium-based batteries preferred | No
C.4 | Outputs:
C.4a) | IEC 60320 output ports: at least 6x type C13 and 1x C19 (10A/16A) | No
C.4b) | Software-controlled outputs | No
C.5 | Output waveform: pure sine wave | No
D. | Availability and Reliability
D.1 | Batteries are excluded from the standard equipment warranty, but must be covered by the same warranty conditions for a 2-year period | No
D.1a) | State warranty terms for batteries
D.1b) | State the period for which the batteries are guaranteed unconditionally
D.2 | State MTBF (mean time before failure) for base system (power-on hours)
E. | System Management
E.1 | Integrated remote management, configuration and monitoring functionality | No
E.1a) | Failure alerts and status warnings via SNMP, SMTP or other mechanism | No
E.1b) | Web standards-based remote management | No
E.1c) | Remote power cycling of individual output ports preferred | No
E.2 | Remote monitoring and alerts:
E.2a) | Status and performance metrics | No
E.2b) | Power status on individual output ports preferred | No
E.2c) | Battery status/failures | No
E.2d) | Component failures | No
E.3 | Support for integration into enterprise-level management suites (e.g. OpenView, SCCM, Tivoli, UniCentre) | No
E.4 | Integrated control panel for information, configuration and administration | No
E.5 | Connectivity:
E.5a) | USB or RS-232 interface | No
E.5b) | 10/100BT Ethernet port | No
E.6 | Security:
E.6a) | Role- or ACL-based management access control (e.g. Operator / Supervisor) | No
E.6b) | Support for industry-standard, secure protocols (e.g. SSH, HTTPS, SSL/TLS) | No
E.6c) | Firmware and software updates digitally signed by OEM to mimise risk of updates preferred | No
E.6d) | Communications security verified by third party preferred | No
E.6e) | Support for IEC 62443-4-2 and UL 2900-1 cybersecurity standards preferred | No
E.7 | Device drivers and software:
E.7a) | Software can be downloaded from a generally-available Web site | No
E.7b) | Software for previous versions of supported OSes must be made available on request | No
E.8 | Firmware updates must be made available free of charge for the entire warranty period | No
E.9 | Documentation for complete solution with configuration and operation guidelines | No
E.10 | System model change lifecycle: at least 12 months from introduction to replacement | No
F. | System enclosure and Environmental Characteristics
F.1 | Default system form factor: rack-mount | No
F.1a) | Form factor is convertible to tower preferred | No
F.1b) | State enclosure size in rack units (u)
F.2 | Power and cooling characteristics:
F.2a) | Power supply: 220/230 VAC ±10%, 50 Hz | No
F.2b) | Tolerance for voltage and frequency fluctuations: UPS must support a sustained 50% load without switching to batteries within 120-270VAC and 50Hz ±15% (acceptable derating at lower voltages will be allowed) | No
F.2c) | IEC 60320 power connectors | No
F.2d) | State maximum power consumption (Watts) for UPS (i.e. while charging batteries at full load) | 9999
F.2e) | State maximum cooling requirements (BTU/hour) for UPS (i.e. while charging batteries at full load) | 9999
F.3 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
G. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
G.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
G.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
G.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
G.3 | Only components that are supported by the OEM may be bundled with the solution | No
G.4 | Operating system support:
G.4a) | Microsoft Windows Server: current and previous version | No
G.4b) | Linux: at least 1 major enterprise distro (Specify distros that the system is certified for in Comments column) | No
G.4c) | Solaris, BSD or other Unix preferred | No
G.4d) | Mainstream hypervisors, incl. VMware, Hyper-V and KVM | No
G.5 | High-level diagram of system architecture (showing interfaces and major components) must be included with submission | No
G.6 | UPS efficiency graph must be included with submission | No
G.7 | Manufacturing certifications:
G.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
G.7b) | ISO 14001: certification for environmental management | No
G.7c) | Reduction of Hazardous Substances (RoHS) | No
G.7d) | State country of manufacture
G.8 | UPS standards compliance (international certification acceptable):
G.8a) | IEC/EN 62040-1: UPS safety requirements | No
G.8b) | IEC/EN 62040-2: UPS EMC requirements | No
G.8c) | IEC/EN 62040-3: UPS efficiency preferred | No
G.8d) | IEC/EN 62040-4: UPS environmental aspects preferred | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
H. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
H.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
H.1a) | Base product _________________________________ | 999999.99
H.1b) | Derivative 1 __________________________________ | 0
H.1c) | Derivative 2 __________________________________ | 0
H.1d) | Derivative 3 __________________________________ | 0
H.1e) | Derivative 4 __________________________________ | 0
H.1f) | Derivative 5 __________________________________ | 0
I. | Services
I.1 | Warranty extensions:
I.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
I.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1d) | Additional SLA/service option ____________________ | 0
I.1e) | Additional SLA/service option ____________________ | 0
I.1f) | Additional SLA/service option ____________________ | 0
I.1g) | Additional SLA/service option ____________________ | 0
I.2 | Installation charge for base eval config | 999999.99
I.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
I.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
J. | Additional Components
J.1 | Extended runtime modules:
J.1a) | Runtime module _______________________________ | 0
J.1b) | Runtime module _______________________________ | 0
J.1c) | Runtime module _______________________________ | 0
J.1d) | Runtime module _______________________________ | 0
J.2 | Replacement batteries:
J.2a) | Battery module _______________________________ | 0
J.2b) | Battery module _______________________________ | 0
J.2c) | Battery module _______________________________ | 0
J.3 | Battery module _______________________________ | 0
J.4 | Power Distribution Units:
J.4a) | PDU: 8 IEC 60320 outputs | 0
J.4b) | PDU _______________________________________ | 0
J.4c) | PDU _______________________________________ | 0
J.4d) | PDU _______________________________________ | 0
J.4e) | Intelligent/managed PDU ________________________ | 0
J.4f) | Intelligent/managed PDU ________________________ | 0
J.4g) | Intelligent/managed PDU ________________________ | 0
J.4h) | Intelligent/managed PDU ________________________ | 0
J.5 | Power cables:
J.5a) | Power cable _________________________________ | 0
J.5b) | Power cable _________________________________ | 0
J.5c) | Power cable _________________________________ | 0
J.5d) | Power cable _________________________________ | 0
J.6 | Remote management:
J.6a) | Other management module ______________________ | 0
J.6b) | Other management module ______________________ | 0
J.6c) | Other management module ______________________ | 0
J.6d) | Other management module ______________________ | 0
J.7 | Software:
J.7a) | Software option _______________________________ | 0
J.7b) | Software option _______________________________ | 0
J.7c) | Software option _______________________________ | 0
J.7d) | Software option _______________________________ | 0
J.8 | Rack-mount rails and tower conversion kit | 0
J.9 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
J.9a) | Additional component __________________________ | 0
J.9b) | Additional component __________________________ | 0
J.9c) | Additional component __________________________ | 0
J.9d) | Additional component __________________________ | 0
J.9e) | Additional component __________________________ | 0
J.9f) | Additional component __________________________ | 0
J.9g) | Additional component __________________________ | 0
J.9h) | Additional component __________________________ | 0
J.9i) | Additional component __________________________ | 0
J.9j) | Additional component __________________________ | 0
J.9k) | Additional component __________________________ | 0
J.9l) | Additional component __________________________ | 0
J.9m) | Additional component __________________________ | 0
J.9n) | Additional component __________________________ | 0
J.9o) | Additional component __________________________ | 0
J.9p) | Additional component __________________________ | 0
J.9q) | Additional component __________________________ | 0
J.9r) | Additional component __________________________ | 0
J.9s) | Additional component __________________________ | 0
J.9t) | Additional component __________________________ | 0

## UPS_OL3
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
UPS_OL3: Advanced on-line UPS
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Advanced single-phase online (double-conversion) uninterruptible power supply | No
A.1a) | Modular design for UPS capacities > 10KVA preferred | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Output capacity: 5 KVA or higher (UPS must be sized to meet the specified wattage) | No
A.4 | Effective load-bearing capacity: 4.5KW or higher with at least 90% efficiency | No
A.5 | Runtime: at power loss, the UPS must maintain power to the full load for at least 5 minutes | No
A.5a) | The UPS must notify attached systems of power failure to allow graceful shutdown | No
A.5b) | Battery must be sized based on client's runtime requirement, if greater than 5 minutes | No
A.6 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.7 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Software included with system:
B.2a) | Client software for latest versions of operating systems as specified | No
B.2b) | Network shutdown software | No
B.2c) | Installation and configuration tools | No
B.2d) | Diagnostic and management tools | No
B.3 | Network management module (SNMP or equivalent) | No
B.4 | Mounting rails (only for rack-mount solutions) | No
B.5 | Services included:
B.5a) | On-site installation and configuration | No
B.5b) | End-user training of at least 1-2 hours | No
C. | System Properties and Functionality
C.1 | UPS capabilities:
C.1a) | Single-phase design for input and output | No
C.1b) | Support for modular design (output >10KVA) preferred | No
C.1c) | State UPS load-bearing rating: Watts
C.1d) | State UPS load-bearing rating: KVA
C.1e) | State runtime at full load for base system (minutes)
C.1f) | Support for extended runtime via battery upgrades | No
C.1g) | State derating coefficient (altitude, temperature, etc.)
C.2 | Runtime:
C.2a) | State baseline runtime support @ 50% load (minutes)
C.2b) | State baseline runtime support @ 100% load (minutes)
C.2c) | State maximum runtime supported with all possible runtime upgrades @ 50% load (minutes)
C.2d) | State maximum runtime supported with all possible runtime upgrades @ 100% load (minutes)
C.2e) | Ability to function and provide clean power while battery is discharged or being serviced | No
C.2f) | Support for high-efficiency/eco mode (>95%) | No
C.2g) | Generator support: THDi < 5% | No
C.2h) | Hypervisor support: ability to integrate into virtualisation management and shut down or migrate virtual servers when power is lost | No
C.3 | Battery functionality and management:
C.3a) | Hot-swappable batteries | No
C.3b) | Integrated battery test and protection mechanisms | No
C.3c) | Battery replacement indicator | No
C.3d) | Charger capacity: batteries must be recharged to 90% capacity in 8 hours | No
C.3e) | Support for optional lithium-based batteries preferred | No
C.4 | Outputs:
C.4a) | IEC 60320 output ports: at least 6x type C13 and 1x C19 (10A/16A), or hard-wired distribution board connection | No
C.4b) | Software-controlled outputs (not for hard-wired) preferred | No
C.4c) | For hard-wired solution: external hard-wired output to client distribution board - sized to load requirements, supplied as part of electrical reticulation | No
C.4d) | In the case of distribution board-connected UPSs, the system must be wired by a certified electrician, who must issue an electrical compliance certificate as part of the solution price. | No
C.5 | Output waveform: pure sine wave | No
D. | Availability and Reliability
D.1 | Batteries are excluded from the standard equipment warranty, but must be covered by the same warranty conditions for a 2-year period | No
D.1a) | Pre-failure warranty (component replaced under warranty on pre-failure warning) for batteries preferred | No
D.1b) | State warranty terms for batteries
D.1c) | State the period for which the batteries are guaranteed unconditionally
D.2 | State MTBF (mean time before failure) for base system (power-on hours)
E. | System Management
E.1 | Integrated remote management, configuration and monitoring functionality | No
E.1a) | Failure alerts and status warnings via SNMP, SMTP or other mechanism | No
E.1b) | Web standards-based remote management | No
E.1c) | Remote power cycling of individual output ports preferred | No
E.2 | Remote monitoring and alerts:
E.2a) | Status and performance metrics | No
E.2b) | Power status on individual output ports preferred | No
E.2c) | Battery status/failures | No
E.2d) | Component failures | No
E.3 | Support for integration into enterprise-level management suites (e.g. OpenView, SCCM, Tivoli, UniCentre) | No
E.4 | Integrated control panel for information, configuration and administration | No
E.5 | Connectivity:
E.5a) | USB or RS-232 interface | No
E.5b) | 10/100BT Ethernet port | No
E.6 | Security:
E.6a) | Role- or ACL-based management access control (e.g. Operator / Supervisor) | No
E.6b) | Support for industry-standard, secure protocols (e.g. SSH, HTTPS, SSL/TLS) | No
E.6c) | Firmware and software updates digitally signed by OEM to mimise risk of updates preferred | No
E.6d) | Communications security verified by third party preferred | No
E.6e) | Support for IEC 62443-4-2 and UL 2900-1 cybersecurity standards preferred | No
E.7 | Device drivers and software:
E.7a) | Software can be downloaded from a generally-available Web site | No
E.7b) | Software for previous versions of supported OSes must be made available on request | No
E.8 | Firmware updates must be made available free of charge for the entire warranty period | No
E.9 | Documentation for complete solution with configuration and operation guidelines | No
E.10 | System model change lifecycle: at least 12 months from introduction to replacement | No
F. | System enclosure and Environmental Characteristics
F.1 | Default system form factor: rack-mount | No
F.1a) | Form factor is convertible to tower preferred | No
F.1b) | State enclosure size in rack units (u)
F.2 | Power and cooling characteristics:
F.2a) | Power supply: 220/230 VAC ±10%, 50 Hz | No
F.2b) | Tolerance for voltage and frequency fluctuations: UPS must support a sustained 50% load without switching to batteries within 120-270VAC and 50Hz ±15% (acceptable derating at lower voltages will be allowed) | No
F.2c) | IEC 60320 power connectors, or direct distribution board (DB) input | No
F.2d) | State maximum power consumption (Watts) for UPS (i.e. while charging batteries at full load) | 9999
F.2e) | State maximum cooling requirements (BTU/hour) for UPS (i.e. while charging batteries at full load) | 9999
F.3 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
G. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
G.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
G.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
G.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
G.3 | Only components that are supported by the OEM may be bundled with the solution | No
G.4 | Operating system support:
G.4a) | Microsoft Windows Server: current and previous version | No
G.4b) | Linux: at least 1 major enterprise distro (Specify distros that the system is certified for in Comments column) | No
G.4c) | Solaris, BSD or other Unix preferred | No
G.4d) | Mainstream hypervisors, incl. VMware, Hyper-V and KVM | No
G.5 | High-level diagram of system architecture (showing interfaces and major components) must be included with submission | No
G.6 | UPS efficiency graph must be included with submission | No
G.7 | Manufacturing certifications:
G.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
G.7b) | ISO 14001: certification for environmental management | No
G.7c) | Reduction of Hazardous Substances (RoHS) | No
G.7d) | State country of manufacture
G.8 | Electrical safety requirements for installations:
G.8a) | Hardwired (DB-wired) systems must be installed according to SANS 0416 | No
G.8b) | All hardwired (DB-wired) systems must be installed by a qualified electrician, and a Certificate of Conformance (CoC) must be issued | No
G.8c) | Hardwired (DB-wired) systems must have a maintenance bypass switch installed as part of the solution | No
G.9 | UPS standards compliance (international certification acceptable):
G.9a) | IEC/EN 62040-1: UPS safety requirements | No
G.9b) | IEC/EN 62040-2: UPS EMC requirements | No
G.9c) | IEC/EN 62040-3: UPS efficiency preferred | No
G.9d) | IEC/EN 62040-4: UPS environmental aspects preferred | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
H. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
H.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
H.1a) | Base product _________________________________ | 999999.99
H.1b) | Derivative 1 __________________________________ | 0
H.1c) | Derivative 2 __________________________________ | 0
H.1d) | Derivative 3 __________________________________ | 0
H.1e) | Derivative 4 __________________________________ | 0
H.1f) | Derivative 5 __________________________________ | 0
I. | Services
I.1 | Warranty extensions:
I.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
I.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1d) | Additional SLA/service option ____________________ | 0
I.1e) | Additional SLA/service option ____________________ | 0
I.1f) | Additional SLA/service option ____________________ | 0
I.1g) | Additional SLA/service option ____________________ | 0
I.2 | Installation charge for base eval config | 999999.99
I.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
I.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
J. | Additional Components
J.1 | Extended runtime modules:
J.1a) | Runtime module _______________________________ | 0
J.1b) | Runtime module _______________________________ | 0
J.1c) | Runtime module _______________________________ | 0
J.1d) | Runtime module _______________________________ | 0
J.2 | Replacement batteries:
J.2a) | Battery module _______________________________ | 0
J.2b) | Battery module _______________________________ | 0
J.2c) | Battery module _______________________________ | 0
J.3 | Battery module _______________________________ | 0
J.4 | Replacement power modules:
J.4a) | Power module ________________________________ | 0
J.4b) | Power module ________________________________ | 0
J.4c) | Power module ________________________________ | 0
J.4d) | Power module ________________________________ | 0
J.5 | Power Distribution Units:
J.5a) | PDU: 8 IEC 60320 outputs | 0
J.5b) | PDU _______________________________________ | 0
J.5c) | PDU _______________________________________ | 0
J.5d) | PDU _______________________________________ | 0
J.5e) | Intelligent/managed PDU ________________________ | 0
J.5f) | Intelligent/managed PDU ________________________ | 0
J.5g) | Intelligent/managed PDU ________________________ | 0
J.5h) | Intelligent/managed PDU ________________________ | 0
J.6 | Power cables:
J.6a) | Power cable _________________________________ | 0
J.6b) | Power cable _________________________________ | 0
J.6c) | Power cable _________________________________ | 0
J.6d) | Power cable _________________________________ | 0
J.7 | Remote management:
J.7a) | Other management module ______________________ | 0
J.7b) | Other management module ______________________ | 0
J.7c) | Other management module ______________________ | 0
J.7d) | Other management module ______________________ | 0
J.8 | Software:
J.8a) | Software option _______________________________ | 0
J.8b) | Software option _______________________________ | 0
J.8c) | Software option _______________________________ | 0
J.8d) | Software option _______________________________ | 0
J.9 | Rack-mount rails and tower conversion kit | 0
J.10 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
J.10a) | Additional component __________________________ | 0
J.10b) | Additional component __________________________ | 0
J.10c) | Additional component __________________________ | 0
J.10d) | Additional component __________________________ | 0
J.10e) | Additional component __________________________ | 0
J.10f) | Additional component __________________________ | 0
J.10g) | Additional component __________________________ | 0
J.10h) | Additional component __________________________ | 0
J.10i) | Additional component __________________________ | 0
J.10j) | Additional component __________________________ | 0
J.10k) | Additional component __________________________ | 0
J.10l) | Additional component __________________________ | 0
J.10m) | Additional component __________________________ | 0
J.10n) | Additional component __________________________ | 0
J.10o) | Additional component __________________________ | 0
J.10p) | Additional component __________________________ | 0
J.10q) | Additional component __________________________ | 0
J.10r) | Additional component __________________________ | 0
J.10s) | Additional component __________________________ | 0
J.10t) | Additional component __________________________ | 0

## UPS_OL4
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
UPS_OL4: Advanced 3-phase on-line UPS
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Advanced three-phase online (double-conversion) uninterruptible power supply | No
A.1a) | Modular design preferred | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Output capacity: 10 KVA or higher (UPS must be sized to meet the specified wattage) | No
A.4 | Effective load-bearing capacity: 9KW or higher with at least 90% efficiency | No
A.5 | Runtime: at power loss, the UPS must maintain power to the full load for at least 5 minutes | No
A.5a) | The UPS must notify attached systems of power failure to allow graceful shutdown | No
A.5b) | Battery must be sized based on client's runtime requirement, if greater than 5 minutes | No
A.6 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.7 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Software included with system:
B.2a) | Client software for latest versions of operating systems as specified | No
B.2b) | Network shutdown software | No
B.2c) | Installation and configuration tools | No
B.2d) | Diagnostic and management tools | No
B.3 | Network management module (SNMP or equivalent) | No
B.4 | Mounting rails (only for rack-mount solutions) | No
B.5 | Services included:
B.5a) | On-site installation and configuration | No
B.5b) | End-user training of at least 1-2 hours | No
C. | System Properties and Functionality
C.1 | UPS capabilities:
C.1a) | 3-phase design for input, single-phase output | No
C.1b) | Support for system-level redundancy (n+1) preferred | No
C.1c) | State UPS load-bearing rating: Watts
C.1d) | State UPS load-bearing rating: KVA
C.1e) | Unity power factor preferred | No
C.1f) | State runtime at full load for base system (minutes)
C.1g) | Support for extended runtime via battery upgrades | No
C.1h) | State derating coefficient (altitude, temperature, etc.)
C.2 | Runtime:
C.2a) | State baseline runtime support @ 50% load (minutes)
C.2b) | State baseline runtime support @ 100% load (minutes)
C.2c) | State maximum runtime supported with all possible runtime upgrades @ 50% load (minutes)
C.2d) | State maximum runtime supported with all possible runtime upgrades @ 100% load (minutes)
C.2e) | Ability to function and provide clean power while battery is discharged or being serviced | No
C.2f) | Support for high-efficiency/eco mode (>95%) | No
C.2g) | Generator support: THDi < 3% | No
C.2h) | Hypervisor support: ability to integrate into virtualisation management and shut down or migrate virtual servers when power is lost | No
C.3 | System capacity:
C.3a) | State range of output sizes (KW) available for proposed system
C.3b) | State range of battery capacities (KWh) available for proposed solution
C.4 | Battery functionality and management:
C.4a) | Hot-swappable batteries | No
C.4b) | Integrated battery test and protection mechanisms | No
C.4c) | Battery replacement indicator | No
C.4d) | Charger capacity: batteries must be recharged to 90% capacity in 10 hours | No
C.4e) | Support for optional lithium-based batteries preferred | No
C.5 | Outputs:
C.5a) | External hard-wired output to client distribution board - sized to load requirements, supplied as part of electrical reticulation | No
C.5b) | In the case of distribution board-connected UPSs, the system must be wired by a certified electrician, who must issue an electrical compliance certificate as part of the solution price. | No
C.6 | Output waveform: pure sine wave | No
D. | Availability and Reliability
D.1 | Batteries are excluded from the standard equipment warranty, but must be covered by the same warranty conditions for a 2-year period | No
D.1a) | Pre-failure warranty (component replaced under warranty on pre-failure warning) for batteries preferred | No
D.1b) | State warranty terms for batteries
D.1c) | State the period for which the batteries are guaranteed unconditionally
D.2 | State MTBF (mean time before failure) for base system (power-on hours)
E. | System Management
E.1 | Integrated remote management, configuration and monitoring functionality | No
E.1a) | Failure alerts and status warnings via SNMP, SMTP or other mechanism | No
E.1b) | Web standards-based remote management | No
E.1c) | Remote power cycling of individual output ports preferred | No
E.2 | Remote monitoring and alerts:
E.2a) | Status and performance metrics | No
E.2b) | Power status on individual output ports preferred | No
E.2c) | Battery status/failures | No
E.2d) | Component failures | No
E.3 | Support for integration into enterprise-level management suites (e.g. OpenView, SCCM, Tivoli, UniCentre) | No
E.4 | Integrated control panel for information, configuration and administration | No
E.5 | Connectivity:
E.5a) | USB or RS-232 interface | No
E.5b) | 10/100BT Ethernet port | No
E.6 | Security:
E.6a) | Role- or ACL-based management access control (e.g. Operator / Supervisor) | No
E.6b) | Support for industry-standard, secure protocols (e.g. SSH, HTTPS, SSL/TLS) | No
E.6c) | Firmware and software updates digitally signed by OEM to mimise risk of updates preferred | No
E.6d) | Communications security verified by third party preferred | No
E.6e) | Support for IEC 62443-4-2 and UL 2900-1 cybersecurity standards preferred | No
E.7 | Device drivers and software:
E.7a) | Software can be downloaded from a generally-available Web site | No
E.7b) | Software for previous versions of supported OSes must be made available on request | No
E.8 | Firmware updates must be made available free of charge for the entire warranty period | No
E.9 | Documentation for complete solution with configuration and operation guidelines | No
E.10 | System model change lifecycle: at least 12 months from introduction to replacement | No
F. | System enclosure and Environmental Characteristics
F.1 | System form factor: stand-alone | No
F.2 | Power and cooling characteristics:
F.2a) | Power supply: 380/400 VAC ±10%, 50 Hz | No
F.2b) | Tolerance for voltage and frequency fluctuations: UPS must support a sustained 50% load without switching to batteries within 250-450VAC and 50Hz ±15% (acceptable derating at lower voltages will be allowed) | No
F.2c) | IEC 60320 power connectors, or direct distribution board (DB) input | No
F.2d) | State maximum power consumption (Watts) for UPS (i.e. while charging batteries at full load) | 9999
F.2e) | State maximum cooling requirements (BTU/hour) for UPS (i.e. while charging batteries at full load) | 9999
F.3 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
G. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
G.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
G.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
G.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
G.3 | Only components that are supported by the OEM may be bundled with the solution | No
G.4 | Operating system support:
G.4a) | Microsoft Windows Server: current and previous version | No
G.4b) | Linux: at least 1 major enterprise distro (Specify distros that the system is certified for in Comments column) | No
G.4c) | Solaris, BSD or other Unix preferred | No
G.4d) | Mainstream hypervisors, incl. VMware, Hyper-V and KVM | No
G.5 | High-level diagram of system architecture (showing interfaces and major components) must be included with submission | No
G.6 | UPS efficiency graph must be included with submission | No
G.7 | Manufacturing certifications:
G.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
G.7b) | ISO 14001: certification for environmental management | No
G.7c) | Reduction of Hazardous Substances (RoHS) | No
G.7d) | State country of manufacture
G.8 | Electrical safety requirements for installations:
G.8a) | Hardwired (DB-wired) systems must be installed according to SANS 0416 | No
G.8b) | All hardwired (DB-wired) systems must be installed by a qualified electrician, and a Certificate of Conformance (CoC) must be issued | No
G.8c) | Hardwired (DB-wired) systems must have a maintenance bypass switch installed as part of the solution | No
G.9 | UPS standards compliance (international certification acceptable):
G.9a) | IEC/EN 62040-1: UPS safety requirements | No
G.9b) | IEC/EN 62040-2: UPS EMC requirements | No
G.9c) | IEC/EN 62040-3: UPS efficiency preferred | No
G.9d) | IEC/EN 62040-4: UPS environmental aspects preferred | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
H. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
H.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
H.1a) | Base product _________________________________ | 999999.99
H.1b) | Derivative 1 __________________________________ | 0
H.1c) | Derivative 2 __________________________________ | 0
H.1d) | Derivative 3 __________________________________ | 0
H.1e) | Derivative 4 __________________________________ | 0
H.1f) | Derivative 5 __________________________________ | 0
I. | Services
I.1 | Warranty extensions:
I.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
I.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1d) | Additional SLA/service option ____________________ | 0
I.1e) | Additional SLA/service option ____________________ | 0
I.1f) | Additional SLA/service option ____________________ | 0
I.1g) | Additional SLA/service option ____________________ | 0
I.2 | Installation charge for base eval config | 999999.99
I.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
I.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
J. | Additional Components
J.1 | Extended runtime modules:
J.1a) | Runtime module _______________________________ | 0
J.1b) | Runtime module _______________________________ | 0
J.1c) | Runtime module _______________________________ | 0
J.1d) | Runtime module _______________________________ | 0
J.2 | Replacement batteries:
J.2a) | Battery module _______________________________ | 0
J.2b) | Battery module _______________________________ | 0
J.2c) | Battery module _______________________________ | 0
J.3 | Battery module _______________________________ | 0
J.4 | Replacement power modules:
J.4a) | Power module ________________________________ | 0
J.4b) | Power module ________________________________ | 0
J.4c) | Power module ________________________________ | 0
J.4d) | Power module ________________________________ | 0
J.5 | Power Distribution Units:
J.5a) | PDU: 8 IEC 60320 outputs | 0
J.5b) | PDU _______________________________________ | 0
J.5c) | PDU _______________________________________ | 0
J.5d) | PDU _______________________________________ | 0
J.5e) | Intelligent/managed PDU ________________________ | 0
J.5f) | Intelligent/managed PDU ________________________ | 0
J.5g) | Intelligent/managed PDU ________________________ | 0
J.5h) | Intelligent/managed PDU ________________________ | 0
J.6 | Power cables:
J.6a) | Power cable _________________________________ | 0
J.6b) | Power cable _________________________________ | 0
J.6c) | Power cable _________________________________ | 0
J.6d) | Power cable _________________________________ | 0
J.7 | Remote management:
J.7a) | Other management module ______________________ | 0
J.7b) | Other management module ______________________ | 0
J.7c) | Other management module ______________________ | 0
J.7d) | Other management module ______________________ | 0
J.8 | Software:
J.8a) | Software option _______________________________ | 0
J.8b) | Software option _______________________________ | 0
J.8c) | Software option _______________________________ | 0
J.8d) | Software option _______________________________ | 0
J.9 | Rack-mount rails and tower conversion kit | 0
J.10 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
J.10a) | Additional component __________________________ | 0
J.10b) | Additional component __________________________ | 0
J.10c) | Additional component __________________________ | 0
J.10d) | Additional component __________________________ | 0
J.10e) | Additional component __________________________ | 0
J.10f) | Additional component __________________________ | 0
J.10g) | Additional component __________________________ | 0
J.10h) | Additional component __________________________ | 0
J.10i) | Additional component __________________________ | 0
J.10j) | Additional component __________________________ | 0
J.10k) | Additional component __________________________ | 0
J.10l) | Additional component __________________________ | 0
J.10m) | Additional component __________________________ | 0
J.10n) | Additional component __________________________ | 0
J.10o) | Additional component __________________________ | 0
J.10p) | Additional component __________________________ | 0
J.10q) | Additional component __________________________ | 0
J.10r) | Additional component __________________________ | 0
J.10s) | Additional component __________________________ | 0
J.10t) | Additional component __________________________ | 0

## UPS_OL5
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
UPS_OL5: 3-phase building UPS
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Three-phase online (double-conversion) uninterruptible power supply for building backup power supply | No
A.1a) | Modular design preferred | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.2a) | System must be installed in conjunction with a backup power system (e.g. generator) | No
A.3 | Output capacity: 50 KVA or higher (UPS must be sized to meet the specified wattage) | No
A.4 | Effective load-bearing capacity: 45KW or higher with at least 90% efficiency | No
A.5 | Runtime: at power loss, the UPS must maintain power to the full load for at least 5 minutes | No
A.5a) | The UPS must notify attached systems of power failure to allow graceful shutdown | No
A.5b) | Battery must be sized based on client's runtime requirement, if greater than 5 minutes | No
A.6 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.7 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Software included with system:
B.2a) | Client software for latest versions of operating systems as specified | No
B.2b) | Network shutdown software | No
B.2c) | Installation and configuration tools | No
B.2d) | Diagnostic and management tools | No
B.3 | Network management module (SNMP or equivalent) | No
B.4 | Mounting rails (only for rack-mount solutions) | No
B.5 | Services included:
B.5a) | On-site installation and configuration | No
B.5b) | End-user training of at least 1-2 hours | No
C. | System Properties and Functionality
C.1 | UPS capabilities:
C.1a) | 3-phase design for input and output | No
C.1b) | Support for parallel installation | No
C.1c) | Support for system-level redundancy (n+1) | No
C.1d) | Hot-swappable power modules preferred | No
C.1e) | State UPS load-bearing rating: Watts
C.1f) | State UPS load-bearing rating: KVA
C.1g) | Unity power factor preferred | No
C.1h) | State runtime at full load for base system (minutes)
C.1i) | Support for extended runtime via battery upgrades | No
C.1j) | State derating coefficient (altitude, temperature, etc.)
C.2 | Runtime:
C.2a) | State baseline runtime support @ 50% load (minutes)
C.2b) | State baseline runtime support @ 100% load (minutes)
C.2c) | State maximum runtime supported with all possible runtime upgrades @ 50% load (minutes)
C.2d) | State maximum runtime supported with all possible runtime upgrades @ 100% load (minutes)
C.2e) | Ability to function and provide clean power while battery is discharged or being serviced | No
C.2f) | Support for high-efficiency/eco mode (>95%) | No
C.2g) | Generator support: THDi < 3% | No
C.2h) | Hypervisor support: ability to integrate into virtualisation management and shut down or migrate virtual servers when power is lost preferred | No
C.3 | System capacity:
C.3a) | State range of output sizes (KW) available for proposed system
C.3b) | State range of battery capacities (KWh) available for proposed solution
C.4 | Battery functionality and management:
C.4a) | Hot-swappable batteries | No
C.4b) | Integrated battery test and protection mechanisms | No
C.4c) | Battery replacement indicator | No
C.4d) | Charger capacity: batteries must be recharged to 90% capacity in 10 hours | No
C.4e) | Support for optional Lithium-Ion batteries preferred | No
C.5 | Outputs:
C.5a) | External hard-wired output to client distribution board - sized to load requirements, supplied as part of electrical reticulation | No
C.5b) | In the case of distribution board-connected UPSs, the system must be wired by a certified electrician, who must issue an electrical compliance certificate as part of the solution price. | No
C.6 | Output waveform: pure sine wave | No
D. | Availability and Reliability
D.1 | Batteries are excluded from the standard equipment warranty, but must be covered by the same warranty conditions for a 2-year period | No
D.1a) | Pre-failure warranty (component replaced under warranty on pre-failure warning) for batteries preferred | No
D.1b) | State warranty terms for batteries
D.1c) | State the period for which the batteries are guaranteed unconditionally
D.2 | State MTBF (mean time before failure) for base system (power-on hours)
E. | System Management
E.1 | Integrated remote management, configuration and monitoring functionality | No
E.1a) | Failure alerts and status warnings via SNMP, SMTP or other mechanism | No
E.1b) | Web standards-based remote management | No
E.1c) | Remote power cycling of individual output ports preferred | No
E.2 | Remote monitoring and alerts:
E.2a) | Status and performance metrics | No
E.2b) | Power status on individual output ports preferred | No
E.2c) | Battery status/failures | No
E.2d) | Component failures | No
E.3 | Support for integration into enterprise-level management suites (e.g. OpenView, SCCM, Tivoli, UniCentre) | No
E.3a) | Support for integration with building management system (BMS) | No
E.4 | Integrated control panel for information, configuration and administration | No
E.5 | Connectivity:
E.5a) | USB or RS-232 interface | No
E.5b) | 10/100BT Ethernet port | No
E.6 | Security:
E.6a) | Role- or ACL-based management access control (e.g. Operator / Supervisor) | No
E.6b) | Support for industry-standard, secure protocols (e.g. SSH, HTTPS, SSL/TLS) | No
E.6c) | Firmware and software updates digitally signed by OEM to mimise risk of updates preferred | No
E.6d) | Communications security verified by third party preferred | No
E.6e) | Support for IEC 62443-4-2 and UL 2900-1 cybersecurity standards preferred | No
E.7 | Device drivers and software:
E.7a) | Software can be downloaded from a generally-available Web site | No
E.7b) | Software for previous versions of supported OSes must be made available on request | No
E.8 | Firmware updates must be made available free of charge for the entire warranty period | No
E.9 | Documentation for complete solution with configuration and operation guidelines | No
E.10 | System model change lifecycle: at least 12 months from introduction to replacement | No
F. | System enclosure and Environmental Characteristics
F.1 | System form factor: stand-alone | No
F.2 | Power and cooling characteristics:
F.2a) | Power supply: 380/400 VAC ±10%, 50 Hz | No
F.2b) | Tolerance for voltage and frequency fluctuations: UPS must support a sustained 50% load without switching to batteries within 250-450VAC and 50Hz ±15% (acceptable derating at lower voltages will be allowed) | No
F.2c) | IEC 60320 power connectors, or direct distribution board (DB) input | No
F.2d) | State maximum power consumption (Watts) for UPS (i.e. while charging batteries at full load) | 9999
F.2e) | State maximum cooling requirements (BTU/hour) for UPS (i.e. while charging batteries at full load) | 9999
F.3 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
G. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
G.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
G.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
G.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
G.3 | Only components that are supported by the OEM may be bundled with the solution | No
G.4 | Operating system support:
G.4a) | Microsoft Windows Server: current and previous version | No
G.4b) | Linux: at least 1 major enterprise distro (Specify distros that the system is certified for in Comments column) | No
G.4c) | Solaris, BSD or other Unix preferred | No
G.4d) | Mainstream hypervisors, incl. VMware, Hyper-V and KVM | No
G.5 | High-level diagram of system architecture (showing interfaces and major components) must be included with submission | No
G.6 | UPS efficiency graph must be included with submission | No
G.7 | Manufacturing certifications:
G.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
G.7b) | ISO 14001: certification for environmental management | No
G.7c) | Reduction of Hazardous Substances (RoHS) | No
G.7d) | State country of manufacture
G.8 | Electrical safety requirements for installations:
G.8a) | Hardwired (DB-wired) systems must be installed according to SANS 0416 | No
G.8b) | All hardwired (DB-wired) systems must be installed by a qualified electrician, and a Certificate of Conformance (CoC) must be issued | No
G.8c) | Hardwired (DB-wired) systems must have a maintenance bypass switch installed as part of the solution | No
G.9 | UPS standards compliance (international certification acceptable):
G.9a) | IEC/EN 62040-1: UPS safety requirements | No
G.9b) | IEC/EN 62040-2: UPS EMC requirements | No
G.9c) | IEC/EN 62040-3: UPS efficiency preferred | No
G.9d) | IEC/EN 62040-4: UPS environmental aspects preferred | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
H. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
H.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
H.1a) | Base product _________________________________ | 999999.99
H.1b) | Derivative 1 __________________________________ | 0
H.1c) | Derivative 2 __________________________________ | 0
H.1d) | Derivative 3 __________________________________ | 0
H.1e) | Derivative 4 __________________________________ | 0
H.1f) | Derivative 5 __________________________________ | 0
I. | Services
I.1 | Warranty extensions:
I.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
I.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1d) | Additional SLA/service option ____________________ | 0
I.1e) | Additional SLA/service option ____________________ | 0
I.1f) | Additional SLA/service option ____________________ | 0
I.1g) | Additional SLA/service option ____________________ | 0
I.2 | Installation charge for base eval config | 999999.99
I.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
I.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
J. | Additional Components
J.1 | Extended runtime modules:
J.1a) | Runtime module _______________________________ | 0
J.1b) | Runtime module _______________________________ | 0
J.1c) | Runtime module _______________________________ | 0
J.1d) | Runtime module _______________________________ | 0
J.2 | Replacement batteries:
J.2a) | Battery module _______________________________ | 0
J.2b) | Battery module _______________________________ | 0
J.2c) | Battery module _______________________________ | 0
J.3 | Battery module _______________________________ | 0
J.4 | Replacement power modules:
J.4a) | Power module ________________________________ | 0
J.4b) | Power module ________________________________ | 0
J.4c) | Power module ________________________________ | 0
J.4d) | Power module ________________________________ | 0
J.5 | Power Distribution Units:
J.5a) | PDU: 8 IEC 60320 outputs | 0
J.5b) | PDU _______________________________________ | 0
J.5c) | PDU _______________________________________ | 0
J.5d) | PDU _______________________________________ | 0
J.5e) | Intelligent/managed PDU ________________________ | 0
J.5f) | Intelligent/managed PDU ________________________ | 0
J.5g) | Intelligent/managed PDU ________________________ | 0
J.5h) | Intelligent/managed PDU ________________________ | 0
J.6 | Power cables:
J.6a) | Power cable _________________________________ | 0
J.6b) | Power cable _________________________________ | 0
J.6c) | Power cable _________________________________ | 0
J.6d) | Power cable _________________________________ | 0
J.7 | Remote management:
J.7a) | Other management module ______________________ | 0
J.7b) | Other management module ______________________ | 0
J.7c) | Other management module ______________________ | 0
J.7d) | Other management module ______________________ | 0
J.8 | Software:
J.8a) | Software option _______________________________ | 0
J.8b) | Software option _______________________________ | 0
J.8c) | Software option _______________________________ | 0
J.8d) | Software option _______________________________ | 0
J.9 | Rack-mount rails and tower conversion kit | 0
J.10 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
J.10a) | Additional component __________________________ | 0
J.10b) | Additional component __________________________ | 0
J.10c) | Additional component __________________________ | 0
J.10d) | Additional component __________________________ | 0
J.10e) | Additional component __________________________ | 0
J.10f) | Additional component __________________________ | 0
J.10g) | Additional component __________________________ | 0
J.10h) | Additional component __________________________ | 0
J.10i) | Additional component __________________________ | 0
J.10j) | Additional component __________________________ | 0
J.10k) | Additional component __________________________ | 0
J.10l) | Additional component __________________________ | 0
J.10m) | Additional component __________________________ | 0
J.10n) | Additional component __________________________ | 0
J.10o) | Additional component __________________________ | 0
J.10p) | Additional component __________________________ | 0
J.10q) | Additional component __________________________ | 0
J.10r) | Additional component __________________________ | 0
J.10s) | Additional component __________________________ | 0
J.10t) | Additional component __________________________ | 0

## UPS_OL6
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
UPS_OL6: 3-phase datacentre UPS
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Three-phase online (double-conversion) uninterruptible power supply for datacentre backup power supply | No
A.1a) | Modular design preferred | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.2a) | System must be installed in conjunction with a backup power system (e.g. generator) | No
A.3 | Output capacity: 50 KVA or higher (UPS must be sized to meet the specified wattage) | No
A.4 | Effective load-bearing capacity: 45KW or higher with at least 90% efficiency | No
A.5 | Runtime: at power loss, the UPS must maintain power to the full load for at least 5 minutes | No
A.5a) | The UPS must notify attached systems of power failure to allow graceful shutdown | No
A.5b) | Battery must be sized based on client's runtime requirement, if greater than 5 minutes | No
A.6 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.7 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Software included with system:
B.2a) | Client software for latest versions of operating systems as specified | No
B.2b) | Network shutdown software | No
B.2c) | Installation and configuration tools | No
B.2d) | Diagnostic and management tools | No
B.3 | Network management module (SNMP or equivalent) | No
B.4 | Mounting rails (only for rack-mount solutions) | No
B.5 | Services included:
B.5a) | On-site installation and configuration | No
B.5b) | End-user training of at least 1-2 hours | No
C. | System Properties and Functionality
C.1 | UPS capabilities:
C.1a) | 3-phase design for input and output | No
C.1b) | Support for parallel installation | No
C.1c) | Support for system-level redundancy (n+1) | No
C.1d) | Hot-swappable power modules preferred | No
C.1e) | State UPS load-bearing rating: Watts
C.1f) | State UPS load-bearing rating: KVA
C.1g) | Unity power factor preferred | No
C.1h) | State runtime at full load for base system (minutes)
C.1i) | Support for extended runtime via battery upgrades | No
C.1j) | State derating coefficient (altitude, temperature, etc.)
C.2 | Runtime:
C.2a) | State baseline runtime support @ 50% load (minutes)
C.2b) | State baseline runtime support @ 100% load (minutes)
C.2c) | State maximum runtime supported with all possible runtime upgrades @ 50% load (minutes)
C.2d) | State maximum runtime supported with all possible runtime upgrades @ 100% load (minutes)
C.2e) | Ability to function and provide clean power while battery is discharged or being serviced | No
C.2f) | Support for high-efficiency/eco mode (>95%) | No
C.2g) | Generator support: THDi < 3% | No
C.2h) | Hypervisor support: ability to integrate into virtualisation management and shut down or migrate virtual servers when power is lost | No
C.3 | System capacity:
C.3a) | State range of output sizes (KW) available for proposed system
C.3b) | State range of battery capacities (KWh) available for proposed solution
C.4 | Battery functionality and management:
C.4a) | Hot-swappable batteries | No
C.4b) | Integrated battery test and protection mechanisms | No
C.4c) | Battery replacement indicator | No
C.4d) | Charger capacity: batteries must be recharged to 90% capacity in 10 hours | No
C.4e) | Support for optional Lithium-Ion batteries preferred | No
C.5 | Outputs:
C.5a) | External hard-wired output to client distribution board - sized to load requirements, supplied as part of electrical reticulation | No
C.5b) | In the case of distribution board-connected UPSs, the system must be wired by a certified electrician, who must issue an electrical compliance certificate as part of the solution price. | No
C.6 | Output waveform: pure sine wave | No
D. | Availability and Reliability
D.1 | Batteries are excluded from the standard equipment warranty, but must be covered by the same warranty conditions for a 2-year period | No
D.1a) | Pre-failure warranty (component replaced under warranty on pre-failure warning) for batteries preferred | No
D.1b) | State warranty terms for batteries
D.1c) | State the period for which the batteries are guaranteed unconditionally
D.2 | State MTBF (mean time before failure) for base system (power-on hours)
E. | System Management
E.1 | Integrated remote management, configuration and monitoring functionality | No
E.1a) | Failure alerts and status warnings via SNMP, SMTP or other mechanism | No
E.1b) | Web standards-based remote management | No
E.1c) | Remote power cycling of individual output ports preferred | No
E.2 | Remote monitoring and alerts:
E.2a) | Status and performance metrics | No
E.2b) | Power status on individual output ports preferred | No
E.2c) | Battery status/failures | No
E.2d) | Component failures | No
E.3 | Support for integration into enterprise-level management suites (e.g. OpenView, SCCM, Tivoli, UniCentre) | No
E.3a) | Support for integration with building management system (BMS) | No
E.4 | Integrated control panel for information, configuration and administration | No
E.5 | Connectivity:
E.5a) | USB or RS-232 interface | No
E.5b) | 10/100BT Ethernet port | No
E.6 | Security:
E.6a) | Role- or ACL-based management access control (e.g. Operator / Supervisor) | No
E.6b) | Support for industry-standard, secure protocols (e.g. SSH, HTTPS, SSL/TLS) | No
E.6c) | Firmware and software updates digitally signed by OEM to mimise risk of updates preferred | No
E.6d) | Communications security verified by third party preferred | No
E.6e) | Support for IEC 62443-4-2 and UL 2900-1 cybersecurity standards preferred | No
E.7 | Device drivers and software:
E.7a) | Software can be downloaded from a generally-available Web site | No
E.7b) | Software for previous versions of supported OSes must be made available on request | No
E.8 | Firmware updates must be made available free of charge for the entire warranty period | No
E.9 | Documentation for complete solution with configuration and operation guidelines | No
E.10 | System model change lifecycle: at least 12 months from introduction to replacement | No
F. | System enclosure and Environmental Characteristics
F.1 | System form factor: stand-alone | No
F.2 | Power and cooling characteristics:
F.2a) | Power supply: 380/400 VAC ±10%, 50 Hz | No
F.2b) | Tolerance for voltage and frequency fluctuations: UPS must support a sustained 50% load without switching to batteries within 250-450VAC and 50Hz ±15% (acceptable derating at lower voltages will be allowed) | No
F.2c) | IEC 60320 power connectors, or direct distribution board (DB) input | No
F.2d) | State maximum power consumption (Watts) for UPS (i.e. while charging batteries at full load) | 9999
F.2e) | State maximum cooling requirements (BTU/hour) for UPS (i.e. while charging batteries at full load) | 9999
F.3 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
G. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
G.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
G.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
G.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
G.3 | Only components that are supported by the OEM may be bundled with the solution | No
G.4 | Operating system support:
G.4a) | Microsoft Windows Server: current and previous version | No
G.4b) | Linux: at least 1 major enterprise distro (Specify distros that the system is certified for in Comments column) | No
G.4c) | Solaris, BSD or other Unix preferred | No
G.4d) | Mainstream hypervisors, incl. VMware, Hyper-V and KVM | No
G.5 | High-level diagram of system architecture (showing interfaces and major components) must be included with submission | No
G.6 | UPS efficiency graph must be included with submission | No
G.7 | Manufacturing certifications:
G.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
G.7b) | ISO 14001: certification for environmental management | No
G.7c) | Reduction of Hazardous Substances (RoHS) | No
G.7d) | State country of manufacture
G.8 | Electrical safety requirements for installations:
G.8a) | Hardwired (DB-wired) systems must be installed according to SANS 0416 | No
G.8b) | All hardwired (DB-wired) systems must be installed by a qualified electrician, and a Certificate of Conformance (CoC) must be issued | No
G.8c) | Hardwired (DB-wired) systems must have a maintenance bypass switch installed as part of the solution | No
G.9 | UPS standards compliance (international certification acceptable):
G.9a) | IEC/EN 62040-1: UPS safety requirements | No
G.9b) | IEC/EN 62040-2: UPS EMC requirements | No
G.9c) | IEC/EN 62040-3: UPS efficiency preferred | No
G.9d) | IEC/EN 62040-4: UPS environmental aspects preferred | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
H. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
H.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
H.1a) | Base product _________________________________ | 999999.99
H.1b) | Derivative 1 __________________________________ | 0
H.1c) | Derivative 2 __________________________________ | 0
H.1d) | Derivative 3 __________________________________ | 0
H.1e) | Derivative 4 __________________________________ | 0
H.1f) | Derivative 5 __________________________________ | 0
I. | Services
I.1 | Warranty extensions:
I.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
I.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
I.1d) | Additional SLA/service option ____________________ | 0
I.1e) | Additional SLA/service option ____________________ | 0
I.1f) | Additional SLA/service option ____________________ | 0
I.1g) | Additional SLA/service option ____________________ | 0
I.2 | Installation charge for base eval config | 999999.99
I.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
I.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
J. | Additional Components
J.1 | Extended runtime modules:
J.1a) | Runtime module _______________________________ | 0
J.1b) | Runtime module _______________________________ | 0
J.1c) | Runtime module _______________________________ | 0
J.1d) | Runtime module _______________________________ | 0
J.2 | Replacement batteries:
J.2a) | Battery module _______________________________ | 0
J.2b) | Battery module _______________________________ | 0
J.2c) | Battery module _______________________________ | 0
J.3 | Battery module _______________________________ | 0
J.4 | Replacement power modules:
J.4a) | Power module ________________________________ | 0
J.4b) | Power module ________________________________ | 0
J.4c) | Power module ________________________________ | 0
J.4d) | Power module ________________________________ | 0
J.5 | Power Distribution Units:
J.5a) | PDU: 8 IEC 60320 outputs | 0
J.5b) | PDU _______________________________________ | 0
J.5c) | PDU _______________________________________ | 0
J.5d) | PDU _______________________________________ | 0
J.5e) | Intelligent/managed PDU ________________________ | 0
J.5f) | Intelligent/managed PDU ________________________ | 0
J.5g) | Intelligent/managed PDU ________________________ | 0
J.5h) | Intelligent/managed PDU ________________________ | 0
J.6 | Power cables:
J.6a) | Power cable _________________________________ | 0
J.6b) | Power cable _________________________________ | 0
J.6c) | Power cable _________________________________ | 0
J.6d) | Power cable _________________________________ | 0
J.7 | Remote management:
J.7a) | Other management module ______________________ | 0
J.7b) | Other management module ______________________ | 0
J.7c) | Other management module ______________________ | 0
J.7d) | Other management module ______________________ | 0
J.8 | Software:
J.8a) | Software option _______________________________ | 0
J.8b) | Software option _______________________________ | 0
J.8c) | Software option _______________________________ | 0
J.8d) | Software option _______________________________ | 0
J.9 | Rack-mount rails and tower conversion kit | 0
J.10 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
J.10a) | Additional component __________________________ | 0
J.10b) | Additional component __________________________ | 0
J.10c) | Additional component __________________________ | 0
J.10d) | Additional component __________________________ | 0
J.10e) | Additional component __________________________ | 0
J.10f) | Additional component __________________________ | 0
J.10g) | Additional component __________________________ | 0
J.10h) | Additional component __________________________ | 0
J.10i) | Additional component __________________________ | 0
J.10j) | Additional component __________________________ | 0
J.10k) | Additional component __________________________ | 0
J.10l) | Additional component __________________________ | 0
J.10m) | Additional component __________________________ | 0
J.10n) | Additional component __________________________ | 0
J.10o) | Additional component __________________________ | 0
J.10p) | Additional component __________________________ | 0
J.10q) | Additional component __________________________ | 0
J.10r) | Additional component __________________________ | 0
J.10s) | Additional component __________________________ | 0
J.10t) | Additional component __________________________ | 0

## Rack_Wb
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
Rack_Wb: Wall-mount cabinet
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Wall-mount communications/network equipment cabinet (wallbox) | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Rack load-carrying capacity:
A.3a) | Maximum load: 5kg / rack unit | No
A.4 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.5 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Power connections and cabling as specified | No
B.3 | Power and cooling modules as required | No
B.4 | Rack doors, panels, shelves and wall mounting options as required | No
B.4a) | Mounting hardware such as screws, nuts, etc. (equipment rails excluded) | No
B.5 | Services included:
B.5a) | On-site installation and configuration | No
C. | System Properties and Functionality
C.1 | Support for cable management of installed systems | No
C.1a) | Top and bottom entryways for cabling | No
C.2 | Rack door capabilities:
C.2a) | Removable door preferred | No
C.2b) | Reversible door preferred | No
C.2c) | Opening angle 160deg+ | No
C.3 | Removable side panels preferred | No
C.3a) | Support for electronic access control preferred | No
C.4 | Support for 0u options preferred | No
C.5 | Support for optional cooling modules (fans) | No
C.6 | Support for basic as well as intelligent/manageable PDUs | No
C.6a) | PDUs bundled with the solution must be OEM-quality, SANS-compliant devices | No
C.7 | Security:
C.7a) | Support for front door lock, and hinge lock for swing-frame systems | No
C.7b) | Same-key support for front and hinge | No
C.8 | Wallboxes must be installed to allow at least 2m clearance above floor level | No
D. | System enclosure and Environmental Characteristics
D.1 | Rack dimensions: At least 4 usable rack units high, must accommodate standard 19" equipment with a depth of at least 300mm | No
D.1a) | State series height range in rack units (u)
D.1b) | Support for >300mm depth preferred | No
D.2 | Structural material: 16-gauge cold rolled mild steel or equivalent; sufficient to bear load of fully-populated cabinet | No
D.2a) | Door and side panels: 18-gauge cold rolled mild steel or equivalent; sufficient to ensure integrity and security of enclosure
D.2b) | Metal must be properly prepared and finished for longevity and durability (multi-layer powder-coating or equivalent) | No
D.3 | Front door included in Base Price | No
D.3a) | For hinged models (swing frame), the collar and hinge mechanism must be included in Base Price
D.4 | Rack load-carrying capacity:
D.4a) | State maximum static load (kg)
D.5 | Support for both front-mount and front+rear-mount equipment | No
D.6 | State maximum BTUs/hour that can be accommodated in base rack (as per base price)
D.6a) | Sufficient cooling must be integrated in the rack (included in Base Price) to support the above BTU requirements (assuming reasonable ambient temperature) | No
D.7 | Rack units must be marked on front and rear posts | No
D.8 | Ingress protection: perforated panels must conform to IP20 (IEC 60529) | No
D.9 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
D.10 | Documentation for complete solution with configuration and operation guidelines | No
E. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
E.1 | Rack dimensions according to IEC 60297-3 family of standards | No
E.2 | Solution must comply with the relevant SANS electrical standards, including earthing and bonding | No
E.3 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
E.3a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
E.4 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
E.5 | Only components that are supported by the OEM may be bundled with the solution | No
E.6 | Rack enclosure certified and supported by equipment OEM (server/storage/network vendor) preferred | No
E.7 | Manufacturing certifications:
E.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
E.7b) | ISO 14001: certification for environmental management | No
E.7c) | Reduction of Hazardous Substances (RoHS) | No
E.7d) | State country of manufacture
E.8 | Electrical safety and EMC certifications for active components in solution (international certification acceptable):
E.8a) | ISO/IEC 62368: Electrical safety | No
E.8b) | CISPR 32 / EN 55032: General EMC requirements | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
F. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
F.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
F.1a) | Base product _________________________________ | 999999.99
F.1b) | Derivative 1 __________________________________ | 0
F.1c) | Derivative 2 __________________________________ | 0
F.1d) | Derivative 3 __________________________________ | 0
F.1e) | Derivative 4 __________________________________ | 0
F.1f) | Derivative 5 __________________________________ | 0
G. | Services
G.1 | Warranty extensions:
G.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
G.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1d) | Additional SLA/service option ____________________ | 0
G.1e) | Additional SLA/service option ____________________ | 0
G.1f) | Additional SLA/service option ____________________ | 0
G.1g) | Additional SLA/service option ____________________ | 0
G.2 | Installation charge for base eval config | 999999.99
G.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
G.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
G.5 | Configuration and installation of equipment in rack per hour | 999999.99
H. | Additional Components
H.1 | Rack power options:
H.1a) | Power Distribution Unit _________________________ | 0
H.1b) | Power Distribution Unit _________________________ | 0
H.1c) | Additional PDU option __________________________ | 0
H.1d) | Additional PDU option __________________________ | 0
H.1e) | Additional PDU option __________________________ | 0
H.2 | Rack cooling options:
H.2a) | Fan module 1 ________________________________ | 0
H.2b) | Fan module 2 ________________________________ | 0
H.2c) | Additional cooling option ________________________ | 0
H.2d) | Additional cooling option ________________________ | 0
H.2e) | Additional cooling option ________________________ | 0
H.3 | Blanking plates:
H.3a) | 1u blanking plate | 0
H.3b) | 2u blanking plate | 0
H.3c) | 3u blanking plate | 0
H.3d) | 4u blanking plate | 0
H.3e) | Additional blanking plate option ___________________ | 0
H.3f) | Additional blanking plate option ___________________ | 0
H.3g) | Additional blanking plate option ___________________ | 0
H.3h) | Additional blanking plate option ___________________ | 0
H.4 | Additional rack components:
H.4a) | Rack plinth kit | 0
H.4b) | Shelf | 0
H.4c) | Additional rack component ______________________ | 0
H.4d) | Additional rack component ______________________ | 0
H.4e) | Additional rack component ______________________ | 0
H.4f) | Additional rack component ______________________ | 0
H.4g) | Additional rack component ______________________ | 0
H.4h) | Additional rack component ______________________ | 0
H.4i) | Additional rack component ______________________ | 0
H.5 | Facility control, monitoring and alerting:
H.5a) | Controller module | 0
H.5b) | Temperature sensor | 0
H.5c) | Moisture sensor | 0
H.5d) | Fire sensor | 0
H.5e) | Camera module | 0
H.5f) | Access control module | 0
H.5g) | Additional management module ___________________ | 0
H.5h) | Additional management module ___________________ | 0
H.5i) | Additional management module ___________________ | 0
H.5j) | Additional management module ___________________ | 0
H.5k) | Additional management module ___________________ | 0
H.6 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
H.6a) | Additional component __________________________ | 0
H.6b) | Additional component __________________________ | 0
H.6c) | Additional component __________________________ | 0
H.6d) | Additional component __________________________ | 0
H.6e) | Additional component __________________________ | 0
H.6f) | Additional component __________________________ | 0
H.6g) | Additional component __________________________ | 0
H.6h) | Additional component __________________________ | 0
H.6i) | Additional component __________________________ | 0
H.6j) | Additional component __________________________ | 0
H.6k) | Additional component __________________________ | 0
H.6l) | Additional component __________________________ | 0
H.6m) | Additional component __________________________ | 0
H.6n) | Additional component __________________________ | 0
H.6o) | Additional component __________________________ | 0
H.6p) | Additional component __________________________ | 0
H.6q) | Additional component __________________________ | 0
H.6r) | Additional component __________________________ | 0
H.6s) | Additional component __________________________ | 0
H.6t) | Additional component __________________________ | 0

## Rack_Net
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
Rack_Net: Network Cabinet
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Stand-alone 19" equipment cabinet, optimised for networking devices and cabling | No
A.2 | Rack load-carrying capacity:
A.2a) | Maximum static (stationary) load: 10kg / rack unit | No
A.2b) | Maximum dynamic load: 8kg / rack unit | No
A.3 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.4 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.5 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Power connections and cabling as specified | No
B.3 | Power and cooling modules as required | No
B.4 | Rack doors, panels, shelves and castors/feet as required | No
B.4a) | Mounting hardware such as screws, nuts, etc. (equipment rails excluded) | No
B.5 | Services included:
B.5a) | On-site installation and configuration | No
C. | System Properties and Functionality
C.1 | Thermal integrity: option for perforated front and rear doors (at least 70%) | No
C.2 | Support for clear, toughened glass front door preferred | No
C.3 | Support for cable management of installed systems | No
C.3a) | Top and bottom entryways for cabling | No
C.4 | Support for 0u options preferred | No
C.5 | Support for removable, lockable castors and levelling feet | No
C.5a) | Castors and feet must be of sufficient strength to support full range of movement and operation with fully-loaded rack | No
C.6 | Stability: rack must be supplied and installed with sufficient support to maintain balance during transport and servicing of equipment | No
C.7 | Rack door capabilities:
C.7a) | Removable doors preferred | No
C.7b) | Reversible doors preferred | No
C.7c) | Support for split rear doors | No
C.7d) | Opening angle 160deg+ | No
C.8 | Removable side panels | No
C.9 | Support for optional cooling modules (fans) | No
C.10 | Support for basic as well as intelligent/manageable PDUs | No
C.10a) | PDUs bundled with the solution must be OEM-quality, SANS-compliant devices | No
C.11 | Security:
C.11a) | Support for both front and rear locks | No
C.11b) | Same-key support for front and rear | No
C.11c) | Lockable side panels preferred | No
C.11d) | Support for electronic access control preferred | No
D. | System enclosure and Environmental Characteristics
D.1 | Rack dimensions: At least 12 usable rack units high, must accommodate standard 19" equipment with a depth of at least 600mm | No
D.1a) | Support for additional slack cable space | No
D.1b) | State series height range in rack units (u)
D.1c) | Support for 1000mm depth option preferred | No
D.2 | Structural material: 16-gauge cold rolled mild steel or equivalent | No
D.2a) | Door and side panels: 18-gauge cold rolled mild steel or equivalent; sufficient to ensure integrity and security of enclosure
D.2b) | Metal must be properly prepared and finished for longevity and durability (multi-layer powder-coating or equivalent) | No
D.3 | Doors (front and rear) and side panels included in Base Price | No
D.4 | Rack load-carrying capacity:
D.4a) | State maximum static load (kg)
D.4b) | State maximum dynamic load (kg)
D.5 | Support for both front-mount and front+rear-mount equipment | No
D.6 | State maximum BTUs/hour that can be accommodated in base rack (as per base price)
D.6a) | Sufficient cooling must be integrated in the rack (included in Base Price) to support the above BTU requirements (assuming reasonable ambient temperature) | No
D.7 | Rack units must be marked on front and rear posts | No
D.8 | Ingress protection: perforated panels must conform to IP20 (IEC 60529) | No
D.9 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
D.10 | Documentation for complete solution with configuration and operation guidelines | No
E. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
E.1 | Rack dimensions according to IEC 60297-3 family of standards | No
E.2 | Solution must comply with the relevant SANS electrical standards, including earthing and bonding | No
E.3 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
E.3a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
E.4 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
E.5 | Only components that are supported by the OEM may be bundled with the solution | No
E.6 | Rack enclosure certified and supported by equipment OEM (server/storage/network vendor) preferred | No
E.7 | Manufacturing certifications:
E.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
E.7b) | ISO 14001: certification for environmental management | No
E.7c) | Reduction of Hazardous Substances (RoHS) | No
E.7d) | State country of manufacture
E.8 | Electrical safety and EMC certifications for active components in solution (international certification acceptable):
E.8a) | ISO/IEC 62368: Electrical safety | No
E.8b) | CISPR 32 / EN 55032: General EMC requirements | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
F. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
F.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
F.1a) | Base product _________________________________ | 999999.99
F.1b) | Derivative 1 __________________________________ | 0
F.1c) | Derivative 2 __________________________________ | 0
F.1d) | Derivative 3 __________________________________ | 0
F.1e) | Derivative 4 __________________________________ | 0
F.1f) | Derivative 5 __________________________________ | 0
F.1g) | Derivative 6 __________________________________ | 0
F.1h) | Derivative 7 __________________________________ | 0
F.1i) | Derivative 8 __________________________________ | 0
F.1j) | Derivative 9 __________________________________ | 0
F.1k) | Derivative 10 _________________________________ | 0
G. | Services
G.1 | Warranty extensions:
G.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
G.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1d) | Additional SLA/service option ____________________ | 0
G.1e) | Additional SLA/service option ____________________ | 0
G.1f) | Additional SLA/service option ____________________ | 0
G.1g) | Additional SLA/service option ____________________ | 0
G.2 | Installation charge for base eval config | 999999.99
G.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
G.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
G.5 | Configuration and installation of equipment in rack per hour | 999999.99
H. | Additional Components
H.1 | Rack power options:
H.1a) | Power Distribution Unit _________________________ | 0
H.1b) | Power Distribution Unit _________________________ | 0
H.1c) | Additional PDU option __________________________ | 0
H.1d) | Additional PDU option __________________________ | 0
H.1e) | Additional PDU option __________________________ | 0
H.1f) | Power cabling and extenders ____________________ | 0
H.1g) | Additional ___________________________________ | 0
H.1h) | Additional ___________________________________ | 0
H.1i) | Additional ___________________________________ | 0
H.1j) | Additional ___________________________________ | 0
H.1k) | Additional ___________________________________ | 0
H.1l) | Additional ___________________________________ | 0
H.2 | Rack cooling options:
H.2a) | Fan module 1 ________________________________ | 0
H.2b) | Fan module 2 ________________________________ | 0
H.2c) | Additional cooling option ________________________ | 0
H.2d) | Additional cooling option ________________________ | 0
H.2e) | Additional cooling option ________________________ | 0
H.3 | Blanking plates:
H.3a) | 1u blanking plate | 0
H.3b) | 2u blanking plate | 0
H.3c) | 3u blanking plate | 0
H.3d) | 4u blanking plate | 0
H.3e) | Additional blanking plate option ___________________ | 0
H.3f) | Additional blanking plate option ___________________ | 0
H.3g) | Additional blanking plate option ___________________ | 0
H.3h) | Additional blanking plate option ___________________ | 0
H.4 | Additional rack components:
H.4a) | Rack plinth kit | 0
H.4b) | Shelf | 0
H.4c) | Additional rack component ______________________ | 0
H.4d) | Additional rack component ______________________ | 0
H.4e) | Additional rack component ______________________ | 0
H.4f) | Additional rack component ______________________ | 0
H.4g) | Additional rack component ______________________ | 0
H.4h) | Additional rack component ______________________ | 0
H.4i) | Additional rack component ______________________ | 0
H.5 | Facility control, monitoring and alerting:
H.5a) | Controller module | 0
H.5b) | Temperature sensor | 0
H.5c) | Moisture sensor | 0
H.5d) | Fire sensor | 0
H.5e) | Camera module | 0
H.5f) | Access control module | 0
H.5g) | Additional management module ___________________ | 0
H.5h) | Additional management module ___________________ | 0
H.5i) | Additional management module ___________________ | 0
H.5j) | Additional management module ___________________ | 0
H.5k) | Additional management module ___________________ | 0
H.6 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
H.6a) | Additional component __________________________ | 0
H.6b) | Additional component __________________________ | 0
H.6c) | Additional component __________________________ | 0
H.6d) | Additional component __________________________ | 0
H.6e) | Additional component __________________________ | 0
H.6f) | Additional component __________________________ | 0
H.6g) | Additional component __________________________ | 0
H.6h) | Additional component __________________________ | 0
H.6i) | Additional component __________________________ | 0
H.6j) | Additional component __________________________ | 0
H.6k) | Additional component __________________________ | 0
H.6l) | Additional component __________________________ | 0
H.6m) | Additional component __________________________ | 0
H.6n) | Additional component __________________________ | 0
H.6o) | Additional component __________________________ | 0
H.6p) | Additional component __________________________ | 0
H.6q) | Additional component __________________________ | 0
H.6r) | Additional component __________________________ | 0
H.6s) | Additional component __________________________ | 0
H.6t) | Additional component __________________________ | 0

## Rack_Srv
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
Rack_Srv: Server Rack
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Stand-alone 19" equipment cabinet, optimised for server and storage systems | No
A.2 | Rack load-carrying capacity:
A.2a) | Maximum static (stationary) load: 20kg / rack unit | No
A.2b) | Maximum dynamic load: 15kg / rack unit | No
A.3 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.4 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.5 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Power connections and cabling as specified | No
B.3 | Power and cooling modules as required | No
B.4 | Rack doors, panels, shelves and castors/feet as required | No
B.4a) | Mounting hardware such as screws, nuts, etc. (equipment rails excluded) | No
B.5 | Services included:
B.5a) | On-site installation and configuration | No
C. | System Properties and Functionality
C.1 | Thermal integrity: perforated front and rear doors (at least 70% perforated) | No
C.2 | Support for clear, toughened glass front door preferred | No
C.3 | Support for cable management of installed systems | No
C.3a) | Top and bottom entryways for cabling | No
C.4 | Support for 0u options preferred | No
C.5 | Support for removable, lockable castors and levelling feet | No
C.5a) | Castors and feet must be of sufficient strength to support full range of movement and operation with fully-loaded rack | No
C.6 | Stability: rack must be supplied and installed with sufficient support to maintain balance during transport and servicing of equipment | No
C.7 | Rack door capabilities:
C.7a) | Removable doors preferred | No
C.7b) | Reversible doors preferred | No
C.7c) | Support for split rear doors | No
C.7d) | Opening angle 160deg+ | No
C.8 | Removable side panels | No
C.9 | Support for optional cooling modules (fans) | No
C.10 | Support for multi-host console with USB and/or IP-based KVM | No
C.11 | Support for basic as well as intelligent/manageable PDUs | No
C.11a) | PDUs bundled with the solution must be OEM-quality, SANS-compliant devices | No
C.12 | Security:
C.12a) | Support for both front and rear locks | No
C.12b) | Same-key support for front and rear | No
C.12c) | Lockable side panels preferred | No
C.12d) | Support for electronic access control preferred | No
D. | System enclosure and Environmental Characteristics
D.1 | Rack dimensions: At least 12 usable rack units high, must accommodate standard 19" equipment with a depth of at least 800mm | No
D.1a) | State series height range in rack units (u)
D.1b) | Support for 1000mm depth option | No
D.1c) | Support for 1200mm depth option preferred | No
D.1d) | Support for 750mm width option preferred | No
D.2 | Structural material: 16-gauge cold rolled mild steel or equivalent; sufficient to bear load of fully-populated cabinet | No
D.2a) | Door and side panels: 18-gauge cold rolled mild steel or equivalent; sufficient to ensure integrity and security of enclosure
D.2b) | Metal must be properly prepared and finished for longevity and durability (multi-layer powder-coating or equivalent) | No
D.3 | Doors (front and rear) and side panels included in Base Price | No
D.4 | Rack load-carrying capacity:
D.4a) | State maximum static load (kg)
D.4b) | State maximum dynamic load (kg)
D.5 | Support for both front-mount and front+rear-mount equipment | No
D.6 | State maximum BTUs/hour that can be accommodated in base rack (as per base price)
D.6a) | Sufficient cooling must be integrated in the rack (included in Base Price) to support the above BTU requirements (assuming reasonable ambient temperature) | No
D.7 | Rack units must be marked on front and rear posts | No
D.8 | Ingress protection: perforated panels must conform to IP20 (IEC 60529) | No
D.9 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
D.10 | Documentation for complete solution with configuration and operation guidelines | No
E. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
E.1 | Rack dimensions according to IEC 60297-3 family of standards | No
E.2 | Solution must comply with the relevant SANS electrical standards, including earthing and bonding | No
E.3 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
E.3a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
E.4 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
E.5 | Only components that are supported by the OEM may be bundled with the solution | No
E.6 | Rack enclosure certified and supported by equipment OEM (server/storage/network vendor) preferred | No
E.7 | Manufacturing certifications:
E.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
E.7b) | ISO 14001: certification for environmental management | No
E.7c) | Reduction of Hazardous Substances (RoHS) | No
E.7d) | State country of manufacture
E.8 | Electrical safety and EMC certifications for active components in solution (international certification acceptable):
E.8a) | ISO/IEC 62368: Electrical safety | No
E.8b) | CISPR 32 / EN 55032: General EMC requirements | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
F. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
F.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
F.1a) | Base product _________________________________ | 999999.99
F.1b) | Derivative 1 __________________________________ | 0
F.1c) | Derivative 2 __________________________________ | 0
F.1d) | Derivative 3 __________________________________ | 0
F.1e) | Derivative 4 __________________________________ | 0
F.1f) | Derivative 5 __________________________________ | 0
F.1g) | Derivative 6 __________________________________ | 0
F.1h) | Derivative 7 __________________________________ | 0
F.1i) | Derivative 8 __________________________________ | 0
F.1j) | Derivative 9 __________________________________ | 0
F.1k) | Derivative 10 _________________________________ | 0
G. | Services
G.1 | Warranty extensions:
G.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
G.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1d) | Additional SLA/service option ____________________ | 0
G.1e) | Additional SLA/service option ____________________ | 0
G.1f) | Additional SLA/service option ____________________ | 0
G.1g) | Additional SLA/service option ____________________ | 0
G.2 | Installation charge for base eval config | 999999.99
G.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
G.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
G.5 | Configuration and installation of equipment in rack per hour | 999999.99
H. | Additional Components
H.1 | Rack console options:
H.1a) | KVM console: integrated LCD monitor, keyboard and pointing device | 0
H.1b) | Keyboard/Video/Mouse (KVM) console switch | 0
H.1c) | KVM to host cable(s) | 0
H.1d) | Additional KVM option __________________________ | 0
H.1e) | Additional KVM option __________________________ | 0
H.1f) | Additional KVM option __________________________ | 0
H.1g) | Additional KVM option __________________________ | 0
H.1h) | Additional KVM option __________________________ | 0
H.2 | Rack power options:
H.2a) | Power Distribution Unit _________________________ | 0
H.2b) | Power Distribution Unit _________________________ | 0
H.2c) | Power Distribution Unit _________________________ | 0
H.2d) | Power Distribution Unit _________________________ | 0
H.2e) | Power cabling and extenders ____________________ | 0
H.2f) | Additional PDU option __________________________ | 0
H.2g) | Additional PDU option __________________________ | 0
H.2h) | Additional PDU option __________________________ | 0
H.2i) | Additional PDU option __________________________ | 0
H.2j) | Additional PDU option __________________________ | 0
H.2k) | Additional PDU option __________________________ | 0
H.3 | Rack cooling options:
H.3a) | Fan module 1 ________________________________ | 0
H.3b) | Fan module 2 ________________________________ | 0
H.3c) | Additional cooling option ________________________ | 0
H.3d) | Additional cooling option ________________________ | 0
H.3e) | Additional cooling option ________________________ | 0
H.4 | Blanking plates:
H.4a) | 1u blanking plate | 0
H.4b) | 2u blanking plate | 0
H.4c) | 3u blanking plate | 0
H.4d) | 4u blanking plate | 0
H.4e) | Additional blanking plate option ___________________ | 0
H.4f) | Additional blanking plate option ___________________ | 0
H.4g) | Additional blanking plate option ___________________ | 0
H.4h) | Additional blanking plate option ___________________ | 0
H.5 | Additional rack components:
H.5a) | Rack plinth kit | 0
H.5b) | Shelf | 0
H.5c) | Additional rack component ______________________ | 0
H.5d) | Additional rack component ______________________ | 0
H.5e) | Additional rack component ______________________ | 0
H.5f) | Additional rack component ______________________ | 0
H.5g) | Additional rack component ______________________ | 0
H.5h) | Additional rack component ______________________ | 0
H.5i) | Additional rack component ______________________ | 0
H.6 | Facility control, monitoring and alerting:
H.6a) | Controller module | 0
H.6b) | Temperature sensor | 0
H.6c) | Moisture sensor | 0
H.6d) | Fire sensor | 0
H.6e) | Camera module | 0
H.6f) | Access control module | 0
H.6g) | Additional management module ___________________ | 0
H.6h) | Additional management module ___________________ | 0
H.6i) | Additional management module ___________________ | 0
H.6j) | Additional management module ___________________ | 0
H.6k) | Additional management module ___________________ | 0
H.7 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
H.7a) | Additional component __________________________ | 0
H.7b) | Additional component __________________________ | 0
H.7c) | Additional component __________________________ | 0
H.7d) | Additional component __________________________ | 0
H.7e) | Additional component __________________________ | 0
H.7f) | Additional component __________________________ | 0
H.7g) | Additional component __________________________ | 0
H.7h) | Additional component __________________________ | 0
H.7i) | Additional component __________________________ | 0
H.7j) | Additional component __________________________ | 0
H.7k) | Additional component __________________________ | 0
H.7l) | Additional component __________________________ | 0
H.7m) | Additional component __________________________ | 0
H.7n) | Additional component __________________________ | 0
H.7o) | Additional component __________________________ | 0
H.7p) | Additional component __________________________ | 0
H.7q) | Additional component __________________________ | 0
H.7r) | Additional component __________________________ | 0
H.7s) | Additional component __________________________ | 0
H.7t) | Additional component __________________________ | 0

## Rack_Env
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
Rack_Env: Environmental Rack
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Stand-alone 19" equipment rack with environmental controls, optimised for deployment in uncontrolled environments | No
A.2 | Rack load-carrying capacity:
A.2a) | Maximum static (stationary) load: 20kg / rack unit | No
A.2b) | Maximum dynamic load: 15kg / rack unit | No
A.3 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.4 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.5 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Power connections and cabling as specified | No
B.3 | Power and cooling modules as required | No
B.4 | Rack doors, panels, shelves and castors/feet as required | No
B.4a) | Mounting hardware such as screws, nuts, etc. (equipment rails excluded) | No
B.5 | Services included:
B.5a) | On-site installation and configuration | No
B.5b) | End-user training of at least 1-2 hours | No
C. | System Properties and Functionality
C.1 | Clear, toughened glass front door | No
C.2 | Integrated environmental control (air-conditioning) for enclosure | No
C.3 | Support for cable management of installed systems | No
C.3a) | Top and bottom entryways for cabling preferred | No
C.4 | Support for 0u options | No
C.5 | Support for removable, lockable castors and levelling feet | No
C.5a) | Castors and feet must be of sufficient strength to support full range of movement and operation with fully-loaded rack | No
C.6 | Stability: rack must be supplied and installed with sufficient support to maintain balance during transport and servicing of equipment | No
C.7 | Rack door capabilities:
C.7a) | Removable doors preferred | No
C.7b) | Reversible doors preferred | No
C.7c) | Support for split rear doors preferred | No
C.7d) | Opening angle 160deg+ | No
C.8 | Support for multi-host console with USB and/or IP-based KVM | No
C.9 | Support for basic as well as intelligent/manageable PDUs | No
C.9a) | PDUs bundled with the solution must be OEM-quality, SANS-compliant devices | No
C.10 | Security:
C.10a) | Support for both front and rear locks | No
C.10b) | Same-key support for front and rear | No
C.10c) | Lockable side panels preferred | No
C.10d) | Support for electronic access control | No
C.10e) | Support for access control logging preferred | No
C.10f) | Support for environment-friendly fire protection | No
D. | System enclosure and Environmental Characteristics
D.1 | Rack dimensions: At least 30 usable rack units high, must accommodate standard 19" equipment with a depth of at least 800mm | No
D.1a) | State series height range in rack units (u)
D.1b) | Support for 1000mm depth option | No
D.1c) | Support for 1200mm depth option preferred | No
D.1d) | Support for 750mm width option preferred | No
D.2 | Structural material: 16-gauge cold rolled mild steel or equivalent; sufficient to bear load of fully-populated cabinet | No
D.2a) | Door and side panels: 18-gauge cold rolled mild steel or equivalent; sufficient to ensure integrity and security of enclosure
D.2b) | Metal must be properly prepared and finished for longevity and durability (multi-layer powder-coating or equivalent) | No
D.3 | Doors (front and rear) and side panels included in Base Price | No
D.4 | Rack load-carrying capacity:
D.4a) | State maximum static load (kg)
D.4b) | State maximum dynamic load (kg)
D.5 | Support for both front-mount and front+rear-mount equipment | No
D.6 | State maximum BTUs/hour that can be accommodated in base rack (as per base price)
D.6a) | Sufficient cooling must be integrated in the rack (included in Base Price) to support the above BTU requirements (assuming reasonable ambient temperature) | No
D.7 | Rack units must be marked on front and rear posts | No
D.8 | Support for environmental, monitoring and control via sensors and other add-on modules | No
D.9 | Ingress protection: support for IP54 (IEC 60529) or equivalent | No
D.10 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
D.11 | Documentation for complete solution with configuration and operation guidelines | No
E. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
E.1 | Rack dimensions according to IEC 60297-3 family of standards | No
E.2 | Solution must comply with the relevant SANS electrical standards, including earthing and bonding | No
E.3 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
E.3a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
E.4 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
E.5 | Only components that are supported by the OEM may be bundled with the solution | No
E.6 | Rack enclosure certified and supported by equipment OEM (server/storage/network vendor) preferred | No
E.7 | Manufacturing certifications:
E.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
E.7b) | ISO 14001: certification for environmental management | No
E.7c) | Reduction of Hazardous Substances (RoHS) | No
E.7d) | State country of manufacture
E.8 | Electrical safety and EMC certifications for active components in solution (international certification acceptable):
E.8a) | ISO/IEC 62368: Electrical safety | No
E.8b) | CISPR 32 / EN 55032: General EMC requirements | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
F. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
F.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
F.1a) | Base product _________________________________ | 999999.99
F.1b) | Derivative 1 __________________________________ | 0
F.1c) | Derivative 2 __________________________________ | 0
F.1d) | Derivative 3 __________________________________ | 0
F.1e) | Derivative 4 __________________________________ | 0
F.1f) | Derivative 5 __________________________________ | 0
F.1g) | Derivative 6 __________________________________ | 0
F.1h) | Derivative 7 __________________________________ | 0
F.1i) | Derivative 8 __________________________________ | 0
F.1j) | Derivative 9 __________________________________ | 0
F.1k) | Derivative 10 _________________________________ | 0
G. | Services
G.1 | Warranty extensions:
G.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
G.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1d) | Additional SLA/service option ____________________ | 0
G.1e) | Additional SLA/service option ____________________ | 0
G.1f) | Additional SLA/service option ____________________ | 0
G.1g) | Additional SLA/service option ____________________ | 0
G.2 | Installation charge for base eval config | 999999.99
G.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
G.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
G.5 | Configuration and installation of equipment in rack per hour | 999999.99
H. | Additional Components
H.1 | Rack console options:
H.1a) | KVM console: integrated LCD monitor, keyboard and pointing device | 0
H.1b) | Keyboard/Video/Mouse (KVM) console switch | 0
H.1c) | KVM to host cable(s) | 0
H.1d) | Additional KVM option __________________________ | 0
H.1e) | Additional KVM option __________________________ | 0
H.1f) | Additional KVM option __________________________ | 0
H.1g) | Additional KVM option __________________________ | 0
H.1h) | Additional KVM option __________________________ | 0
H.2 | Rack power options:
H.2a) | Power Distribution Unit _________________________ | 0
H.2b) | Power Distribution Unit _________________________ | 0
H.2c) | Power Distribution Unit _________________________ | 0
H.2d) | Power Distribution Unit _________________________ | 0
H.2e) | Power cabling and extenders ____________________ | 0
H.2f) | Additional PDU option __________________________ | 0
H.2g) | Additional PDU option __________________________ | 0
H.2h) | Additional PDU option __________________________ | 0
H.2i) | Additional PDU option __________________________ | 0
H.2j) | Additional PDU option __________________________ | 0
H.2k) | Additional PDU option __________________________ | 0
H.3 | Rack cooling options:
H.3a) | Fan module 1 ________________________________ | 0
H.3b) | Fan module 2 ________________________________ | 0
H.3c) | Additional cooling option ________________________ | 0
H.3d) | Additional cooling option ________________________ | 0
H.3e) | Additional cooling option ________________________ | 0
H.4 | Blanking plates:
H.4a) | 1u blanking plate | 0
H.4b) | 2u blanking plate | 0
H.4c) | 3u blanking plate | 0
H.4d) | 4u blanking plate | 0
H.4e) | Additional blanking plate option ___________________ | 0
H.4f) | Additional blanking plate option ___________________ | 0
H.4g) | Additional blanking plate option ___________________ | 0
H.4h) | Additional blanking plate option ___________________ | 0
H.5 | Additional rack components:
H.5a) | Rack plinth kit | 0
H.5b) | Shelf | 0
H.5c) | Additional rack component ______________________ | 0
H.5d) | Additional rack component ______________________ | 0
H.5e) | Additional rack component ______________________ | 0
H.5f) | Additional rack component ______________________ | 0
H.5g) | Additional rack component ______________________ | 0
H.5h) | Additional rack component ______________________ | 0
H.5i) | Additional rack component ______________________ | 0
H.6 | Facility control, monitoring and alerting:
H.6a) | Controller module | 0
H.6b) | Temperature sensor | 0
H.6c) | Moisture sensor | 0
H.6d) | Fire sensor | 0
H.6e) | Camera module | 0
H.6f) | Access control module | 0
H.6g) | Additional management module ___________________ | 0
H.6h) | Additional management module ___________________ | 0
H.6i) | Additional management module ___________________ | 0
H.6j) | Additional management module ___________________ | 0
H.6k) | Additional management module ___________________ | 0
H.7 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
H.7a) | Additional component __________________________ | 0
H.7b) | Additional component __________________________ | 0
H.7c) | Additional component __________________________ | 0
H.7d) | Additional component __________________________ | 0
H.7e) | Additional component __________________________ | 0
H.7f) | Additional component __________________________ | 0
H.7g) | Additional component __________________________ | 0
H.7h) | Additional component __________________________ | 0
H.7i) | Additional component __________________________ | 0
H.7j) | Additional component __________________________ | 0

## Rack_AV
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
Rack_AV: Audiovisual Rack
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Stand-alone 19" equipment cabinet, optimised for audiovisual applications, incl. with boardroom integration options | No
A.2 | Rack load-carrying capacity:
A.2a) | Maximum static (stationary) load: 10kg / rack unit | No
A.2b) | Maximum dynamic load: 8kg / rack unit | No
A.3 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.4 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.5 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Power connections and cabling as specified | No
B.3 | Power and cooling modules as required | No
B.4 | Rack doors, panels, shelves and castors/feet as required | No
B.4a) | Mounting hardware such as screws, nuts, etc. (equipment rails excluded) | No
B.5 | Services included:
B.5a) | On-site installation and configuration | No
C. | System Properties and Functionality
C.1 | Noise level of rack when installed (including all equipment and cooling) must be within acceptable levels for boardrooms (<42dBA) | No
C.2 | External finish on rack must be adaptable to client decor requirements (e.g. specific colour or wood finish) | No
C.3 | Support for clear, toughened glass front door preferred | No
C.4 | Support for cable management of installed systems | No
C.4a) | Top and bottom entryways for cabling preferred | No
C.5 | Support for 0u options preferred | No
C.6 | Support for removable, lockable castors and levelling feet | No
C.6a) | Castors and feet must be of sufficient strength to support full range of movement and operation with fully-loaded rack | No
C.7 | Stability: rack must be supplied and installed with sufficient support to maintain balance during transport and servicing of equipment | No
C.8 | Rack door capabilities:
C.8a) | Removable doors preferred | No
C.8b) | Reversible doors preferred | No
C.8c) | Support for split rear doors preferred | No
C.8d) | Opening angle 160deg+ | No
C.9 | Removable side panels preferred | No
C.10 | Support for optional cooling modules (fans) | No
C.11 | Support for basic as well as intelligent/manageable PDUs | No
C.11a) | PDUs bundled with the solution must be OEM-quality, SANS-compliant devices | No
C.12 | Security:
C.12a) | Support for both front and rear locks | No
C.12b) | Same-key support for front and rear | No
C.12c) | Lockable side panels preferred | No
C.12d) | Support for electronic access control preferred | No
C.13 | Documentation for complete solution with configuration and operation guidelines | No
D. | System enclosure and Environmental Characteristics
D.1 | Rack dimensions: At least 12 usable rack units high, must accommodate standard 19" equipment with a depth of at least 600mm | No
D.1a) | State series height range in rack units (u)
D.1b) | Racks >30u must be at least 800mm deep | No
D.1c) | Support for 800mm depth option preferred | No
D.2 | Structural material: 16-gauge cold rolled mild steel or equivalent; sufficient to bear load of fully-populated cabinet | No
D.2a) | Door and side panels: 18-gauge cold rolled mild steel or equivalent; sufficient to ensure integrity and security of enclosure
D.2b) | Metal must be properly prepared and finished for longevity and durability (multi-layer powder-coating or equivalent) | No
D.3 | Doors (front and rear) and side panels included in Base Price | No
D.4 | Rack load-carrying capacity:
D.4a) | State maximum static load (kg)
D.4b) | State maximum dynamic load (kg)
D.5 | Support for both front-mount and front+rear-mount equipment | No
D.6 | State maximum BTUs/hour that can be accommodated in base rack (as per base price)
D.6a) | Sufficient cooling must be integrated in the rack (included in Base Price) to support the above BTU requirements (assuming reasonable ambient temperature) | No
D.7 | Rack units must be marked on front and rear posts | No
D.8 | Ingress protection: perforated panels must conform to IP20 (IEC 60529) | No
D.9 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
E. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
E.1 | Rack dimensions according to IEC 60297-3 family of standards | No
E.2 | Solution must comply with the relevant SANS electrical standards, including earthing and bonding | No
E.3 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
E.3a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
E.4 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
E.5 | Only components that are supported by the OEM may be bundled with the solution | No
E.6 | Rack enclosure certified and supported by equipment OEM (AV vendor) preferred | No
E.7 | Manufacturing certifications:
E.7a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
E.7b) | ISO 14001: certification for environmental management | No
E.7c) | Reduction of Hazardous Substances (RoHS) | No
E.7d) | State country of manufacture
E.8 | Electrical safety and EMC certifications for active components in solution (international certification acceptable):
E.8a) | ISO/IEC 62368: Electrical safety | No
E.8b) | CISPR 32 / EN 55032: General EMC requirements | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
F. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
F.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
F.1a) | Base product _________________________________ | 999999.99
F.1b) | Derivative 1 __________________________________ | 0
F.1c) | Derivative 2 __________________________________ | 0
F.1d) | Derivative 3 __________________________________ | 0
F.1e) | Derivative 4 __________________________________ | 0
F.1f) | Derivative 5 __________________________________ | 0
F.1g) | Derivative 6 __________________________________ | 0
F.1h) | Derivative 7 __________________________________ | 0
F.1i) | Derivative 8 __________________________________ | 0
F.1j) | Derivative 9 __________________________________ | 0
F.1k) | Derivative 10 _________________________________ | 0
G. | Services
G.1 | Warranty extensions:
G.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
G.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1d) | Additional SLA/service option ____________________ | 0
G.1e) | Additional SLA/service option ____________________ | 0
G.1f) | Additional SLA/service option ____________________ | 0
G.1g) | Additional SLA/service option ____________________ | 0
G.2 | Installation charge for base eval config | 999999.99
G.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
G.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
G.5 | Configuration and installation of equipment in rack per hour | 999999.99
H. | Additional Components
H.1 | Rack power options:
H.1a) | Power Distribution Unit _________________________ | 0
H.1b) | Power Distribution Unit _________________________ | 0
H.1c) | Power Distribution Unit _________________________ | 0
H.1d) | Power Distribution Unit _________________________ | 0
H.1e) | Power cabling and extenders ____________________ | 0
H.1f) | Additional PDU option __________________________ | 0
H.1g) | Additional PDU option __________________________ | 0
H.1h) | Additional PDU option __________________________ | 0
H.1i) | Additional PDU option __________________________ | 0
H.1j) | Additional PDU option __________________________ | 0
H.1k) | Additional PDU option __________________________ | 0
H.2 | Rack cooling options:
H.2a) | Fan module 1 ________________________________ | 0
H.2b) | Fan module 2 ________________________________ | 0
H.2c) | Additional cooling option ________________________ | 0
H.2d) | Additional cooling option ________________________ | 0
H.2e) | Additional cooling option ________________________ | 0
H.3 | Blanking plates:
H.3a) | 1u blanking plate | 0
H.3b) | 2u blanking plate | 0
H.3c) | 3u blanking plate | 0
H.3d) | 4u blanking plate | 0
H.3e) | Additional blanking plate option ___________________ | 0
H.3f) | Additional blanking plate option ___________________ | 0
H.3g) | Additional blanking plate option ___________________ | 0
H.3h) | Additional blanking plate option ___________________ | 0
H.4 | Additional rack components:
H.4a) | Rack plinth kit | 0
H.4b) | Shelf | 0
H.4c) | Additional rack component ______________________ | 0
H.4d) | Additional rack component ______________________ | 0
H.4e) | Additional rack component ______________________ | 0
H.4f) | Additional rack component ______________________ | 0
H.4g) | Additional rack component ______________________ | 0
H.4h) | Additional rack component ______________________ | 0
H.4i) | Additional rack component ______________________ | 0
H.5 | Facility control, monitoring and alerting:
H.5a) | Controller module | 0
H.5b) | Temperature sensor | 0
H.5c) | Moisture sensor | 0
H.5d) | Fire sensor | 0
H.5e) | Camera module | 0
H.5f) | Access control module | 0
H.5g) | Additional management module ___________________ | 0
H.5h) | Additional management module ___________________ | 0
H.5i) | Additional management module ___________________ | 0
H.5j) | Additional management module ___________________ | 0
H.5k) | Additional management module ___________________ | 0
H.6 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
H.6a) | Additional component __________________________ | 0
H.6b) | Additional component __________________________ | 0
H.6c) | Additional component __________________________ | 0
H.6d) | Additional component __________________________ | 0
H.6e) | Additional component __________________________ | 0
H.6f) | Additional component __________________________ | 0
H.6g) | Additional component __________________________ | 0
H.6h) | Additional component __________________________ | 0
H.6i) | Additional component __________________________ | 0
H.6j) | Additional component __________________________ | 0
H.6k) | Additional component __________________________ | 0
H.6l) | Additional component __________________________ | 0
H.6m) | Additional component __________________________ | 0
H.6n) | Additional component __________________________ | 0
H.6o) | Additional component __________________________ | 0
H.6p) | Additional component __________________________ | 0
H.6q) | Additional component __________________________ | 0
H.6r) | Additional component __________________________ | 0
H.6s) | Additional component __________________________ | 0
H.6t) | Additional component __________________________ | 0

## Env_Mon
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
Env_Mon: Environmental monitoring
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Environmental monitoring and control solution including sensors, devices and connectivity to enable remote monitoring, management and security of data center environments | No
A.2 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.3 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the Request for Quotation/Proposal (RFQ/RFP) | No
A.4 | OEM must provide support to integrate the product into existing or new management systems and infrastructure implemented by Government Departments | No
A.5 | All required components, software, functionality and licences for the entire SLA period must be included in the total solution cost | No
A.6 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Solution Price. All other components are priced separately in Section 2.
B.1 | Fully functional solution as specified in Section 1, including support SLA, documentation and onsite delivery | No
B.2 | Environmental monitoring system, including all components (sensors, access control, connectivity) required for end-user requirement | No
B.2a) | Set of modules, sensors and devices for basic environmental monitoring, expandable as required | No
B.3 | Software included:
B.3a) | Software license(s) as required for entire SLA period (up-front licence cost) | No
B.4 | Services included:
B.4a) | On-site installation and configuration | No
B.4b) | End-user training of at least 1-2 hours | No
C. | System Properties and Functionality
C.1 | Modular system with scalability from basic remote monitoring for a single rack to datacentre-wide coverage with many inputs and outputs | No
C.2 | Centralised portal/dashboard with status, statistics, alerts, reports and remote control functionality | No
C.3 | High-level and detail view of all managed devices/systems showing status, utilisation, location, alerts, etc. | No
C.4 | Monitoring of the following datacentre systems/components supported:
C.4a) | Environmental parameters | No
C.4b) | Server, storage and network equipment | No
C.4c) | HVAC status | No
C.4d) | Electricity status and usage preferred | No
C.4e) | Asset management preferred | No
C.4f) | Security - access control, intrusion detection and video surveillance preferred | No
C.5 | Selection of sensors, components and devices available depending on user monitoring requirements and existing infrastructure | No
C.5a) | Sensor types supported: temperature, humidity, smoke, moisture, contact | No
C.5b) | Support for CCTV cameras preferred | No
C.6 | Support for all SITA-certified datacentre systems, as well as standards-based systems installed in Government | No
C.7 | Support for integration into enterprise-level management suites (e.g. OpenView, SCCM, Tivoli, UniCentre) | No
C.8 | User-customisable reporting capability | No
C.9 | Pro-active monitoring of managed devices with customisable alarms for preventative and remedial actions | No
C.9a) | Support for alarms via SNMP, e-mail, SMS, as well as visual and audible notifications within facility | No
C.10 | Remote device control via web interface | No
C.11 | Agentless management preferred | No
C.11a) | Describe the agent requirement, if applicable
C.12 | Support for a large population of devices, sufficient for Government entity rolling out the solution | No
C.12a) | State maximum number of devices supported
C.13 | Support for backup and restore of remote device configurations | No
C.14 | Automated discovery of networked systems (servers, storage arrays, switches, UPSs, etc.) | No
C.15 | Automatic software updates preferred | No
C.16 | State current software version of product (if applicable)
C.17 | Connectivity:
C.17a) | 10/100BT Ethernet port | No
C.17b) | Support for alternative network connection as backup (e.g. 3G WWAN) | No
C.18 | Power supply: 220/230 VAC ±10%, 50 Hz | No
C.18a) | Support for backup battery preferred | No
C.19 | Security:
C.19a) | OEMs must ensure that the device/solution is as secure as possible by continuously monitoring and making available fixes for vulnerabilities via firmware and software updates | No
C.19b) | Support for industry-standard, secure protocols (e.g. SSH, HTTPS, SSL/TLS) | No
C.19c) | Role- or ACL-based management access control (e.g. Operator / Supervisor) | No
C.19d) | Integration into enterprise directories for authentication and management of users | No
C.19e) | Firmware and software updates digitally signed by OEM to mimise risk of updates preferred | No
C.19f) | Communications security verified by third party preferred | No
D. | Standards, Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation
D.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
D.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
D.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
D.3 | Only components that are supported by the OEM may be bundled with the solution | No
D.4 | Network standards:
D.4a) | Full support for TCP/IP stack and related protocols (e.g. DHCP, DNS) | No
D.4b) | Support for both IPv4 and IPv6 preferred | No
D.4c) | Support for dual-stack operation (simultaneous IPv4 and IPv6) | No
D.4d) | Support for SNMP or equivalent | No
D.4e) | Support for LDAP or equivalent | No
D.5 | Product must be focussed on and designed for enterprise, professional or business environments. Consumer-grade products will not be accepted | No
D.6 | Manufacturing certifications (if applicable):
D.6a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
D.6b) | ISO 14001: certification for environmental management | No
D.6c) | ISO 2500x standards for software quality preferred | No
D.6d) | State country of manufacture
D.7 | High-level diagram of system architecture (showing interfaces and major components) must be included with submission | No
E. | Management, Availability and Reliability
E.1 | Centralised remote management functionality, including discovery, configuration, monitoring and reporting | No
E.1a) | Support for status monitoring and alerts/alarms via SNMP or alternative mechanisms such as SMTP | No
E.1b) | Web standards-based remote management | No
E.1c) | Support for backup and restore of device configuration | No
E.1d) | Support for centralised, secure remote software updates preferred | No
E.2 | Software updates and upgrades will be made available free of charge for the entire SLA period | No
E.3 | OEM must ensure via its partners that sufficient spare parts and support resources are available at all times to meet SLA duration and turnaround times. SITA must be informed by the OEM if it cannot meet this obligation | No
E.4 | Firmware and software updates (security and bug fixes) will be made available free of charge for the entire SLA period | No
E.5 | Documentation for complete solution with configuration and operation guidelines | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
Note: | Pricing represents OEM ceiling prices only, and are SOLELY for use in an INDICATIVE TCO calculation. It is not a quote, will not be used for negotation, and will not be used in any tender.
F. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
F.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
F.1a) | Base product _________________________________ | 999999.99
F.1b) | Derivative 1 __________________________________ | 0
F.1c) | Derivative 2 __________________________________ | 0
F.1d) | Derivative 3 __________________________________ | 0
F.1e) | Derivative 4 __________________________________ | 0
F.1f) | Derivative 5 __________________________________ | 0
G. | Services
G.1 | Warranty/SLA upgrades (upliftment of standard support):
G.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
G.1b) | Guaranteed NBD fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1d) | Additional SLA/service option ____________________ | 0
G.1e) | Additional SLA/service option ____________________ | 0
G.1f) | Additional SLA/service option ____________________ | 0
G.1g) | Additional SLA/service option ____________________ | 0
G.2 | Installation charge for base eval config | 999999.99
G.3 | Hourly rate for additional installation services (over and above base eval config), e.g. software, drivers, AD integration | 999999.99
G.4 | Price for additional technical support per hour (excluding standard support or maintenance) | 999999.99
G.5 | Additional professsional services such as training, consultation, integration, migration (must be directly related to this specific solution) | 999999.99
H. | Additional Components
H.1 | Monitoring and security components:
H.1a) | Temperature sensor | 0
H.1b) | Moisture/leak sensor | 0
H.1c) | Smoke sensor | 0
H.1d) | Vibration sensor | 0
H.1e) | Dry contact sensor | 0
H.1f) | Door switch | 0
H.1g) | Door lock module | 0
H.1h) | Access control module | 0
H.1i) | Surveillance camera module | 0
H.1j) | Backup power for monitoring system | 0
H.1k) | Additional component __________________________ | 0
H.1l) | Additional component __________________________ | 0
H.1m) | Additional component __________________________ | 0
H.1n) | Additional component __________________________ | 0
H.1o) | Additional component __________________________ | 0
H.1p) | Additional component __________________________ | 0
H.1q) | Additional component __________________________ | 0
H.1r) | Additional component __________________________ | 0
H.1s) | Additional component __________________________ | 0
H.1t) | Additional component __________________________ | 0
H.2 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
H.2a) | Additional component __________________________ | 0
H.2b) | Additional component __________________________ | 0
H.2c) | Additional component __________________________ | 0
H.2d) | Additional component __________________________ | 0
H.2e) | Additional component __________________________ | 0
H.2f) | Additional component __________________________ | 0
H.2g) | Additional component __________________________ | 0
H.2h) | Additional component __________________________ | 0
H.2i) | Additional component __________________________ | 0
H.2j) | Additional component __________________________ | 0
H.2k) | Additional component __________________________ | 0
H.2l) | Additional component __________________________ | 0
H.2m) | Additional component __________________________ | 0
H.2n) | Additional component __________________________ | 0
H.2o) | Additional component __________________________ | 0
H.2p) | Additional component __________________________ | 0
H.2q) | Additional component __________________________ | 0
H.2r) | Additional component __________________________ | 0
H.2s) | Additional component __________________________ | 0
H.2t) | Additional component __________________________ | 0
H.2u) | Additional component __________________________ | 0
H.2v) | Additional component __________________________ | 0
H.2w) | Additional component __________________________ | 0
H.2x) | Additional component __________________________ | 0
H.2y) | Additional component __________________________ | 0

## Infra_Mgmt
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
Infra_Mgmt: Infrastructure management tools
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | System and infrastructure management and monitoring tools/software, providing alerts, configuration, deployment support and remote control to enable cost and labour reduction and/or value-added services for data and switching centre solutions | No
A.2 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Except where specifically noted in the RFP/RFQ, solutions must include all components specified here, including all required accessories, capabilities and licences, and services including installation and configuration | No
A.3 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the Request for Quotation/Proposal (RFQ/RFP) | No
A.4 | OEM must provide support to integrate the product into existing or new management systems and infrastructure implemented by Government Departments | No
A.5 | All required components, software, functionality and licences for the entire SLA period must be included in the total solution cost | No
A.6 | Support included in solution price: countrywide on-site with full coverage for entire solution, including labour, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Solution Price. All other components are priced separately in Section 2.
B.1 | Fully functional solution as specified in Section 1, including support SLA, documentation and onsite delivery | No
B.2 | Remote system management, configuration and monitoring functionality | No
B.3 | Software included:
B.3a) | Software license(s) as required for entire SLA period (up-front licence cost) | No
B.3b) | Set of functionality for basic systems management, expandable as required | No
B.3c) | SDK and/or supporting software for target platforms as specified | No
B.4 | Services included:
B.4a) | On-site installation and configuration | No
B.4b) | End-user (client administrator) training of at least 1-2 hours | No
C. | System Properties and Functionality
C.1 | Selection of management services and capabilities depending on user requirements and existing infrastructure | No
C.1a) | Centralised portal/dashboard with system and device status, statistics, alerts, health monitoring, reporting and remote control functionality | No
C.2 | High-level and detail view of all managed devices/systems showing status, utilisation, location, alerts, etc. | No
C.3 | Support for all SITA-certified Srv&Stor systems, as well as standards-based systems installed in Government | No
C.4 | Remote monitoring and management of the following datacentre systems/components supported:
C.4a) | Server, storage and network equipment | No
C.4b) | Electricity status and usage | No
C.4c) | HVAC status | No
C.4d) | Environmental parameters | No
C.4e) | Asset management preferred | No
C.4f) | Security - access control, intrusion detection and video surveillance preferred | No
C.5 | Automated discovery of networked systems (servers, storage arrays, UPSs, etc.) | No
C.6 | Support for integration into enterprise-level management suites (e.g. OpenView, SCCM, Tivoli, UniCentre) | No
C.7 | User-customisable reporting capability | No
C.8 | Pro-active monitoring of managed devices with customisable alarms for preventative and remedial actions | No
C.8a) | Support for alarms via SNMP, e-mail, SMS, as well as visual and audible notifications within facility | No
C.8b) | Support for monitoring via industrial protocols, e.g. Modbus preferred | No
C.9 | Support for integration into third-party systems and infrastructure via e.g. web services, API or SDK | No
C.10 | Support for remote device control via web interface | No
C.11 | Support for agentless device management preferred | No
C.11a) | Describe the agent requirement, if applicable
C.12 | Support for a large population of devices, sufficient for Government entity rolling out the solution | No
C.12a) | State maximum number of devices supported
C.13 | Support for backup and restore of remote device configurations | No
C.14 | Automatic software updates preferred | No
C.15 | State current software version of product (if applicable)
C.16 | Security:
C.16a) | OEMs must ensure that the device/solution is as secure as possible by continuously monitoring and making available fixes for vulnerabilities via firmware and software updates | No
C.16b) | Statement or certification of device/system integrity: contains no known cybersecurity vulnerabilities, backdoors or other mechanisms to compromise system security | No
C.16c) | Support for industry-standard, secure protocols (e.g. SSH, HTTPS, SSL/TLS) | No
C.16d) | Support for 2-factor authentication (2FA) preferred | No
C.16e) | Role- or ACL-based management access control (e.g. Operator / Supervisor) | No
C.16f) | Integration into enterprise directories for authentication and management of users | No
C.16g) | Firmware and software updates digitally signed by OEM to mimise risk of updates preferred | No
C.16h) | Communications security verified by third party preferred | No
D. | Standards, Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation
D.1 | Network standards:
D.1a) | Full support for TCP/IP stack and related protocols (e.g. DHCP, DNS) | No
D.1b) | Support for both IPv4 and IPv6 | No
D.1c) | Support for dual-stack operation (simultaneous IPv4 and IPv6) | No
D.1d) | Support for SNMP | No
D.1e) | Support for LDAP | No
D.2 | Product must be focussed on and designed for enterprise, professional or business environments. Consumer-grade products will not be accepted | No
D.3 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
D.3a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
D.4 | Manufacturing certifications (if applicable):
D.4a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
D.4b) | ISO 14001: certification for environmental management | No
D.4c) | ISO 2500x standards for software quality preferred | No
D.4d) | State country of manufacture
E. | Management, Availability and Reliability
E.1 | Centralised remote management functionality, including discovery, configuration, monitoring and reporting | No
E.1a) | Support for status monitoring and alerts/alarms via SNMP or alternative mechanisms such as SMTP | No
E.1b) | Web standards-based remote management | No
E.1c) | Support for backup and restore of device configuration | No
E.1d) | Support for centralised, secure remote software updates preferred | No
E.2 | Software updates (security and bug fixes) will be made available free of charge for the entire SLA period | No
E.3 | OEM must ensure via its partners that sufficient spare parts and support resources are available at all times to meet SLA duration and turnaround times. SITA must be informed by the OEM if it cannot meet this obligation | No
E.4 | Documentation for complete solution with configuration and operation guidelines | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | This Section contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary components and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
Note: | Pricing represents OEM ceiling prices only, and are SOLELY for use in an INDICATIVE TCO calculation. It is not a quote, will not be used for negotation, and will not be used in any tender.
F. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
F.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1 (as a costing guideline, use 500 device licences):
F.1a) | Base product _________________________________ | 999999.99
F.1b) | Derivative 1 __________________________________ | 0
F.1c) | Derivative 2 __________________________________ | 0
F.1d) | Derivative 3 __________________________________ | 0
F.1e) | Derivative 4 __________________________________ | 0
F.1f) | Derivative 5 __________________________________ | 0
G. | Services
G.1 | Warranty/SLA upgrades (upliftment of standard support):
G.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
G.1b) | Guaranteed NBD fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
G.1d) | Additional SLA/service option ____________________ | 0
G.1e) | Additional SLA/service option ____________________ | 0
G.1f) | Additional SLA/service option ____________________ | 0
G.1g) | Additional SLA/service option ____________________ | 0
G.2 | Installation charge for base eval config | 999999.99
G.3 | Hourly rate for additional installation services (over and above base eval config), e.g. software, drivers, AD integration | 999999.99
G.4 | Price for additional technical support per hour (excluding standard support or maintenance) | 999999.99
G.5 | Additional professsional services such as training, consultation, integration, migration (must be directly related to this specific solution) | 999999.99
H. | Additional Components
H.1 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
H.1a) | Additional component __________________________ | 0
H.1b) | Additional component __________________________ | 0
H.1c) | Additional component __________________________ | 0
H.1d) | Additional component __________________________ | 0
H.1e) | Additional component __________________________ | 0
H.1f) | Additional component __________________________ | 0
H.1g) | Additional component __________________________ | 0
H.1h) | Additional component __________________________ | 0
H.1i) | Additional component __________________________ | 0
H.1j) | Additional component __________________________ | 0
H.1k) | Additional component __________________________ | 0
H.1l) | Additional component __________________________ | 0
H.1m) | Additional component __________________________ | 0
H.1n) | Additional component __________________________ | 0
H.1o) | Additional component __________________________ | 0

## BESS1
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
BESS1: Entry-level BESS solution
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Basic power backup and energy storage solution, including inverter and batteries, with optional solar generation using PV panels. Designed, installed and maintained according to Government electrical standards | No
A.1a) | Modular solution with configurable inverter, batteries and optional PV components with power capacity of at least 3KW | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Output capacity: 3KW or higher (solution must be sized to meet client's required output) | No
A.4 | Runtime: in case of grid power loss, the system must maintain power to 25% of the full load for at least 4 hours | No
A.4a) | Battery capacity: at least 3KWh (must be sized based on client's runtime requirement) | No
A.4b) | Battery capacity must be expandable based on end-user system requirements | No
A.5 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.6 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
A.6a) | Batteries must covered by the standard warranty for a 10-year period | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Inverter as specified | No
B.3 | Battery as specified | No
B.4 | Solar modules as specified (if required) | No
B.5 | Mounting components as required | No
B.6 | Management connection (LAN, WLAN or WAN) | No
B.7 | Software included:
B.7a) | Monitoring application (web-, mobile- or cloud-based) | No
B.7b) | Installation and configuration tools | No
B.7c) | Diagnostic and management tools | No
B.8 | Services included:
B.8a) | Solution sizing and design | No
B.8b) | On-site installation and configuration, including wiring into site distribution board | No
B.8c) | Certificate of Compliance (CoC) issued by qualified electrician | No
B.8d) | End-user training of at least 1-2 hours | No
C. | System Properties and Functionality
C.1 | In case of grid failure, system must switch over to backup power in <10ms | No
C.2 | Intelligent system controller to manage inverter functionality | No
C.3 | System bypass switch for maintenance | No
C.4 | Support for various types of energy sources/storage: Grid, battery, PV, generator | No
C.4a) | Support for energy priority settings (e.g. solar / battery / grid / generator) | No
C.5 | Inverter capabilities:
C.5a) | Single-phase, hybrid, grid-tied inverter | No
C.5b) | Support for multiple operating modes, incl. hybrid, on-grid, off-grid, UPS, etc | No
C.5c) | State inverter load-bearing rating: KW
C.5d) | Output waveform: pure sine wave | No
C.5e) | Efficiency: 90% | No
C.5f) | Generator support: THDi < 3% preferred | No
C.5g) | VOC (voltage open circuit) > 150V | No
C.5h) | Support for parallel installation preferred | No
C.5i) | Support for grid feed-in (disableable) preferred | No
C.5j) | Support for various types of loads, including standard IT equipment (e.g. servers, switches) and motor-type devices such as air-conditioners | No
C.6 | Battery subsystem capabilities:
C.6a) | Integrated battery management system (BMS) providing battery health, protection and capacity management | No
C.6b) | Intelligent charger to optimise battery lifespan and performance | No
C.6c) | Battery chemistry: only LiFePO4 or better allowed | No
C.6d) | Battery charge/discharge rate: at least 1C | No
C.6e) | State max supported battery charge/discharge rate
C.6f) | State runtime at full load for base system (hours)
C.6g) | Charger capacity: batteries must be recharged to 90% capacity in 10 hours | No
C.6h) | State maximum charge current supported (Amps)
C.7 | Photovoltaic capabilities:
C.7a) | MPPT charge controller | No
C.7b) | Dual MPPT controllers preferred | No
C.7c) | Individual PV panel capacity: at least 450W | No
C.7d) | State maximum PV input current supported (Amps)
C.8 | Hard-wired output to client distribution board - sized to load requirements, supplied as part of electrical reticulation | No
C.8a) | Wire gauge of electrical cable according to system characteristics (amps, distance), best practice and manufacturer recommendation (CoC impact) | No
C.9 | The system must be wired by a certified electrician, who must issue an electrical compliance certificate (CoC) as part of the solution price | No
C.10 | System capacity:
C.10a) | State range of output sizes (KW) available for proposed system
C.10b) | State range of battery capacities (KWh) available for proposed solution
C.10c) | State range of PV capacities (KWp) available for proposed solution
C.11 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
C.11a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
C.12 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
D. | System Management
D.1 | Integrated remote management, configuration and monitoring functionality | No
D.1a) | Failure alerts and status warnings via SNMP, SMTP or other industry-standard mechanism preferred | No
D.1b) | Web standards-based remote management preferred | No
D.2 | User-accessible control panel for information, configuration and administration | No
D.3 | Monitoring and alerts:
D.3a) | Embedded sensors for all major components and inputs (e.g. temperature, grid, DC) | No
D.3b) | Status and performance metrics | No
D.3c) | Power status on different power sources (grid, PV, battery, etc.) | No
D.3d) | Component status/failures | No
D.3e) | Statistics and logs of system/power status over time | No
D.4 | Connectivity:
D.4a) | LAN, WLAN or WAN | No
D.4b) | USB or serial (RS-232/485) interface | No
D.4c) | CAN bus for communicating with system components | No
D.5 | State warranty terms for batteries
D.5a) | State the period for which the batteries are guaranteed unconditionally
D.6 | Security:
D.6a) | Support for physical and logical security | No
D.6b) | Password-protected remote monitoring | No
D.7 | Firmware and software updates (security and bug fixes) will be made available free of charge for the entire SLA period | No
D.8 | Documentation for complete solution with configuration and operation guidelines | No
E. | System enclosure and Environmental Characteristics
E.1 | System form factor: stand-alone, wall- or rack-mount | No
E.2 | Environmental sealing: dust- and water-proof to allow flexible deployment outside controlled environments if required - IP54 | No
E.3 | Power and cooling characteristics:
E.3a) | Grid power supply: 220/230 VAC ±10%, 50 Hz | No
E.3b) | Direct distribution board (DB) input and ouput | No
E.3c) | State overhead power consumption (Watts) for inverter (Overhead/Inefficiency = Total power draw - Output load) | 9999
E.3d) | Integrated cooling system to ensure reliable operation of all components) | No
E.4 | Safety features:
E.4a) | Surge protection | No
E.4b) | Overload protection | No
E.4c) | Over-temperature protection | No
E.4d) | Short-circuit protection | No
E.5 | Solution must be properly earthed and bonded according to SABS standards and industry best practices (CoC impact) | No
E.6 | Maximum acoustic noise level for base system: 65 dB(A) according to ISO 9296 (higher noise levels will be allowed for devices that significantly exceed specification) | No
E.6a) | State maximum noise level in dB(A) | 9999
F. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
F.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
F.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
F.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
F.3 | Only components that are supported by the OEM may be bundled with the solution | No
F.4 | High-level diagram of system architecture (showing major components and interfaces) must be included with submission | No
F.5 | Manufacturing certifications:
F.5a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
F.5b) | ISO 14001: certification for environmental management | No
F.5c) | Reduction of Hazardous Substances (RoHS) | No
F.5d) | State country of manufacture
F.6 | Electrical safety and EMC certifications for active components in solution (international certification acceptable):
F.6a) | Hardwired (DB-connected) systems must be installed according to SANS 0416 | No
F.6b) | All hardwired (DB-connected) systems must be installed by a qualified electrician, and a Certificate of Conformance (CoC) must be issued | No
F.6c) | Hardwired (DB-connected) systems must have a maintenance bypass switch installed as part of the solution | No
F.6d) | ISO/IEC 62368: Electrical safety | No
F.6e) | CISPR 32 / EN 55032: General EMC requirements | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | Section 2 contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
G. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
G.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
G.1a) | Base product _________________________________ | 999999.99
G.1b) | Component/Derivative 1 ________________________ | 0
G.1c) | Component/Derivative 2 ________________________ | 0
G.1d) | Component/Derivative 3 ________________________ | 0
G.1e) | Component/Derivative 4 ________________________ | 0
G.1f) | Component/Derivative 5 ________________________ | 0
G.1g) | Component/Derivative 6 ________________________ | 0
G.1h) | Component/Derivative 7 ________________________ | 0
G.1i) | Component/Derivative 8 ________________________ | 0
G.1j) | Component/Derivative 9 ________________________ | 0
G.1k) | Component/Derivative 10 _______________________ | 0
H. | Services
H.1 | Warranty extensions:
H.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
H.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1d) | Additional SLA/service option ____________________ | 0
H.1e) | Additional SLA/service option ____________________ | 0
H.1f) | Additional SLA/service option ____________________ | 0
H.1g) | Additional SLA/service option ____________________ | 0
H.2 | Installation charge for base eval config | 999999.99
H.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
H.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
I. | Additional Components
I.1 | Battery modules:
I.1a) | Battery module _______________________________ | 999999.99
I.1b) | Battery module _______________________________ | 999999.99
I.1c) | Battery module _______________________________ | 0
I.1d) | Battery module _______________________________ | 0
I.1e) | Battery module _______________________________ | 0
I.2 | PV panel modules:
I.2a) | PV module ___________________________________ | 0
I.2b) | PV module ___________________________________ | 0
I.2c) | PV module ___________________________________ | 0
I.2d) | PV module ___________________________________ | 0
I.2e) | PV module ___________________________________ | 0
I.3 | Remote management:
I.3a) | Management comms module _____________________ | 0
I.3b) | Other management module ______________________ | 0
I.3c) | Other management module ______________________ | 0
I.3d) | Other management module ______________________ | 0
I.4 | Software:
I.4a) | Software option _______________________________ | 0
I.4b) | Software option _______________________________ | 0
I.4c) | Software option _______________________________ | 0
I.4d) | Software option _______________________________ | 0
I.5 | Mounting solutions:
I.5a) | Rack-mount rails ______________________________ | 0
I.5b) | Wall-mount brackets ___________________________ | 0
I.5c) | Other mounting option __________________________ | 0
I.5d) | Other mounting option __________________________ | 0
I.5e) | Other mounting option __________________________ | 0
I.5f) | Other mounting option __________________________ | 0
I.6 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
I.6a) | Additional component __________________________ | 0
I.6b) | Additional component __________________________ | 0
I.6c) | Additional component __________________________ | 0
I.6d) | Additional component __________________________ | 0
I.6e) | Additional component __________________________ | 0
I.6f) | Additional component __________________________ | 0
I.6g) | Additional component __________________________ | 0
I.6h) | Additional component __________________________ | 0
I.6i) | Additional component __________________________ | 0
I.6j) | Additional component __________________________ | 0
I.6k) | Additional component __________________________ | 0
I.6l) | Additional component __________________________ | 0
I.6m) | Additional component __________________________ | 0
I.6n) | Additional component __________________________ | 0
I.6o) | Additional component __________________________ | 0
I.6p) | Additional component __________________________ | 0
I.6q) | Additional component __________________________ | 0
I.6r) | Additional component __________________________ | 0
I.6s) | Additional component __________________________ | 0
I.6t) | Additional component __________________________ | 0

## BESS2
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
BESS2: Midrange BESS solution
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Midrange power backup and energy storage solution, including inverter and batteries, with optional solar generation using PV panels. Designed, installed and maintained according to Government electrical standards | No
A.1a) | Modular solution with configurable inverter, batteries and optional PV components with power capacity of at least 5KW | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Output capacity: 5KW or higher (solution must be sized to meet client's required output) | No
A.4 | Runtime: in case of grid power loss, the system must maintain power to 25% of the full load for at least 4 hours | No
A.4a) | Battery capacity: at least 5KWh (must be sized based on client's runtime requirement) | No
A.4b) | Battery capacity must be expandable based on end-user system requirements | No
A.5 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.6 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
A.6a) | Batteries must covered by the standard warranty for a 10-year period | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Inverter as specified | No
B.3 | Battery as specified | No
B.4 | Solar modules as specified (if required) | No
B.5 | Mounting components as required | No
B.6 | Management connection (LAN, WLAN or WAN) | No
B.7 | Software included:
B.7a) | Monitoring application (web-, mobile- or cloud-based) | No
B.7b) | Installation and configuration tools | No
B.7c) | Diagnostic and management tools | No
B.8 | Services included:
B.8a) | Solution sizing and design | No
B.8b) | On-site installation and configuration, including wiring into site distribution board | No
B.8c) | Certificate of Compliance (CoC) issued by qualified electrician | No
B.8d) | End-user training of at least 1-2 hours | No
C. | System Properties and Functionality
C.1 | In case of grid failure, system must switch over to backup power in <10ms | No
C.2 | Intelligent system controller to manage inverter functionality | No
C.3 | System bypass switch for maintenance | No
C.4 | Support for various types of energy sources/storage: Grid, battery, PV, generator | No
C.4a) | Support for energy priority settings (e.g. solar / battery / grid / generator) | No
C.5 | Inverter capabilities:
C.5a) | Single-phase, hybrid, grid-tied inverter | No
C.5b) | Support for multiple operating modes, incl. hybrid, on-grid, off-grid, UPS, etc | No
C.5c) | State inverter load-bearing rating: KW
C.5d) | Output waveform: pure sine wave | No
C.5e) | Efficiency: 90% | No
C.5f) | Generator support: THDi < 3% | No
C.5g) | VOC (voltage open circuit) > 200V | No
C.5h) | Support for parallel installation | No
C.5i) | Support for grid feed-in (disableable) | No
C.5j) | Support for various types of loads, including standard IT equipment (e.g. servers, switches) and motor-type devices such as air-conditioners | No
C.6 | Battery subsystem capabilities:
C.6a) | Integrated battery management system (BMS) providing battery health, protection and capacity management | No
C.6b) | Intelligent charger to optimise battery lifespan and performance | No
C.6c) | Battery chemistry: only LiFePO4 or better allowed | No
C.6d) | Battery charge/discharge rate: at least 1C | No
C.6e) | State max supported battery charge/discharge rate
C.6f) | State runtime at full load for base system (hours)
C.6g) | Charger capacity: batteries must be recharged to 90% capacity in 10 hours | No
C.6h) | State maximum charge current supported (Amps)
C.7 | Photovoltaic capabilities:
C.7a) | Dual MPPT charge controllers | No
C.7b) | 3 MPPT controllers preferred | No
C.7c) | Individual PV panel capacity: at least 450W | No
C.7d) | State maximum PV input current supported (Amps)
C.8 | Hard-wired output to client distribution board - sized to load requirements, supplied as part of electrical reticulation | No
C.8a) | Wire gauge of electrical cable according to system characteristics (amps, distance), best practice and manufacturer recommendation (CoC impact) | No
C.9 | The system must be wired by a certified electrician, who must issue an electrical compliance certificate (CoC) as part of the solution price | No
C.10 | System capacity:
C.10a) | State range of output sizes (KW) available for proposed system
C.10b) | State range of battery capacities (KWh) available for proposed solution
C.10c) | State range of PV capacities (KWp) available for proposed solution
C.11 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
C.11a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
C.12 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
D. | System Management
D.1 | Integrated remote management, configuration and monitoring functionality | No
D.1a) | Failure alerts and status warnings via SNMP, SMTP or other industry-standard mechanism preferred | No
D.1b) | Web standards-based remote management preferred | No
D.2 | User-accessible control panel for information, configuration and administration | No
D.3 | Monitoring and alerts:
D.3a) | Embedded sensors for all major components and inputs (e.g. temperature, grid, DC) | No
D.3b) | Status and performance metrics | No
D.3c) | Power status on different power sources (grid, PV, battery, etc.) | No
D.3d) | Component status/failures | No
D.3e) | Statistics and logs of system/power status over time | No
D.4 | Connectivity:
D.4a) | LAN, WLAN or WAN | No
D.4b) | USB or serial (RS-232/485) interface | No
D.4c) | CAN bus for communicating with system components | No
D.5 | State warranty terms for batteries
D.5a) | State the period for which the batteries are guaranteed unconditionally
D.6 | Security:
D.6a) | Support for physical and logical security | No
D.6b) | Password-protected remote monitoring | No
D.7 | Firmware and software updates (security and bug fixes) will be made available free of charge for the entire SLA period | No
D.8 | Documentation for complete solution with configuration and operation guidelines | No
E. | System enclosure and Environmental Characteristics
E.1 | System form factor: stand-alone, wall- or rack-mount | No
E.2 | Environmental sealing: dust- and water-proof to allow flexible deployment outside controlled environments if required - IP54 | No
E.3 | Power and cooling characteristics:
E.3a) | Grid power supply: 220/230 VAC ±10%, 50 Hz | No
E.3b) | Direct distribution board (DB) input and ouput | No
E.3c) | State overhead power consumption (Watts) for inverter (Overhead/Inefficiency = Total power draw - Output load) | 9999
E.3d) | Integrated cooling system to ensure reliable operation of all components) | No
E.4 | Safety features:
E.4a) | Surge protection | No
E.4b) | Overload protection | No
E.4c) | Over-temperature protection | No
E.4d) | Short-circuit protection | No
E.5 | Solution must be properly earthed and bonded according to SABS standards and industry best practices (CoC impact) | No
E.6 | Maximum acoustic noise level for base system: 65 dB(A) according to ISO 9296 (higher noise levels will be allowed for devices that significantly exceed specification) | No
E.6a) | State maximum noise level in dB(A) | 9999
F. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
F.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
F.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
F.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
F.3 | Only components that are supported by the OEM may be bundled with the solution | No
F.4 | High-level diagram of system architecture (showing major components and interfaces) must be included with submission | No
F.5 | Manufacturing certifications:
F.5a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
F.5b) | ISO 14001: certification for environmental management | No
F.5c) | Reduction of Hazardous Substances (RoHS) | No
F.5d) | State country of manufacture
F.6 | Electrical safety and EMC certifications for active components in solution (international certification acceptable):
F.6a) | Hardwired (DB-connected) systems must be installed according to SANS 0416 | No
F.6b) | All hardwired (DB-connected) systems must be installed by a qualified electrician, and a Certificate of Conformance (CoC) must be issued | No
F.6c) | Hardwired (DB-connected) systems must have a maintenance bypass switch installed as part of the solution | No
F.6d) | ISO/IEC 62368: Electrical safety | No
F.6e) | CISPR 32 / EN 55032: General EMC requirements | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | Section 2 contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
G. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
G.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
G.1a) | Base product _________________________________ | 999999.99
G.1b) | Component/Derivative 1 ________________________ | 0
G.1c) | Component/Derivative 2 ________________________ | 0
G.1d) | Component/Derivative 3 ________________________ | 0
G.1e) | Component/Derivative 4 ________________________ | 0
G.1f) | Component/Derivative 5 ________________________ | 0
G.1g) | Component/Derivative 6 ________________________ | 0
G.1h) | Component/Derivative 7 ________________________ | 0
G.1i) | Component/Derivative 8 ________________________ | 0
G.1j) | Component/Derivative 9 ________________________ | 0
G.1k) | Component/Derivative 10 _______________________ | 0
H. | Services
H.1 | Warranty extensions:
H.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
H.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1d) | Additional SLA/service option ____________________ | 0
H.1e) | Additional SLA/service option ____________________ | 0
H.1f) | Additional SLA/service option ____________________ | 0
H.1g) | Additional SLA/service option ____________________ | 0
H.2 | Installation charge for base eval config | 999999.99
H.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
H.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
I. | Additional Components
I.1 | Battery modules:
I.1a) | Battery module _______________________________ | 999999.99
I.1b) | Battery module _______________________________ | 999999.99
I.1c) | Battery module _______________________________ | 0
I.1d) | Battery module _______________________________ | 0
I.1e) | Battery module _______________________________ | 0
I.2 | PV panel modules:
I.2a) | PV module ___________________________________ | 0
I.2b) | PV module ___________________________________ | 0
I.2c) | PV module ___________________________________ | 0
I.2d) | PV module ___________________________________ | 0
I.2e) | PV module ___________________________________ | 0
I.3 | Remote management:
I.3a) | Management comms module _____________________ | 0
I.3b) | Other management module ______________________ | 0
I.3c) | Other management module ______________________ | 0
I.3d) | Other management module ______________________ | 0
I.4 | Software:
I.4a) | Software option _______________________________ | 0
I.4b) | Software option _______________________________ | 0
I.4c) | Software option _______________________________ | 0
I.4d) | Software option _______________________________ | 0
I.5 | Mounting solutions:
I.5a) | Rack-mount rails ______________________________ | 0
I.5b) | Wall-mount brackets ___________________________ | 0
I.5c) | Other mounting option __________________________ | 0
I.5d) | Other mounting option __________________________ | 0
I.5e) | Other mounting option __________________________ | 0
I.5f) | Other mounting option __________________________ | 0
I.6 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
I.6a) | Additional component __________________________ | 0
I.6b) | Additional component __________________________ | 0
I.6c) | Additional component __________________________ | 0
I.6d) | Additional component __________________________ | 0
I.6e) | Additional component __________________________ | 0
I.6f) | Additional component __________________________ | 0
I.6g) | Additional component __________________________ | 0
I.6h) | Additional component __________________________ | 0
I.6i) | Additional component __________________________ | 0
I.6j) | Additional component __________________________ | 0
I.6k) | Additional component __________________________ | 0
I.6l) | Additional component __________________________ | 0
I.6m) | Additional component __________________________ | 0
I.6n) | Additional component __________________________ | 0
I.6o) | Additional component __________________________ | 0
I.6p) | Additional component __________________________ | 0
I.6q) | Additional component __________________________ | 0
I.6r) | Additional component __________________________ | 0
I.6s) | Additional component __________________________ | 0
I.6t) | Additional component __________________________ | 0

## BESS3
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
BESS3: Advanced BESS solution
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Advanced power backup and energy storage solution, including inverter and batteries, with optional solar generation using PV panels. Designed, installed and maintained according to Government electrical standards | No
A.1a) | Modular solution with configurable inverter, batteries and optional PV components with power capacity of at least 8KW | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Output capacity: 8KW or higher (solution must be sized to meet client's required output) | No
A.4 | Runtime: in case of grid power loss, the system must maintain power to 25% of the full load for at least 4 hours | No
A.4a) | Battery capacity: at least 8KWh (must be sized based on client's runtime requirement) | No
A.4b) | Battery capacity must be expandable based on end-user system requirements | No
A.5 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.6 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
A.6a) | Batteries must covered by the standard warranty for a 10-year period | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Inverter as specified | No
B.3 | Battery as specified | No
B.4 | Solar modules as specified (if required) | No
B.5 | Mounting components as required | No
B.6 | Management connection (LAN, WLAN or WAN) | No
B.7 | Software included:
B.7a) | Monitoring application (web-, mobile- or cloud-based) | No
B.7b) | Installation and configuration tools | No
B.7c) | Diagnostic and management tools | No
B.8 | Services included:
B.8a) | Solution sizing and design | No
B.8b) | On-site installation and configuration, including wiring into site distribution board | No
B.8c) | Certificate of Compliance (CoC) issued by qualified electrician | No
B.8d) | End-user training of at least 1-2 hours | No
C. | System Properties and Functionality
C.1 | In case of grid failure, system must switch over to backup power in <10ms | No
C.2 | Intelligent system controller to manage inverter functionality | No
C.3 | System bypass switch for maintenance | No
C.4 | Support for various types of energy sources/storage: Grid, battery, PV, generator | No
C.4a) | Support for energy priority settings (e.g. solar / battery / grid / generator) | No
C.5 | Inverter capabilities:
C.5a) | Single-phase, hybrid, grid-tied inverter | No
C.5b) | Support for multiple operating modes, incl. hybrid, on-grid, off-grid, UPS, etc | No
C.5c) | State inverter load-bearing rating: KW
C.5d) | Output waveform: pure sine wave | No
C.5e) | Efficiency: 90% | No
C.5f) | Generator support: THDi < 3% | No
C.5g) | VOC (voltage open circuit) > 300V | No
C.5h) | Support for parallel installation | No
C.5i) | Support for grid feed-in (disableable) | No
C.5j) | Support for various types of loads, including standard IT equipment (e.g. servers, switches) and motor-type devices such as air-conditioners | No
C.6 | Battery subsystem capabilities:
C.6a) | Integrated battery management system (BMS) providing battery health, protection and capacity management | No
C.6b) | Intelligent charger to optimise battery lifespan and performance | No
C.6c) | Battery chemistry: only LiFePO4 or better allowed | No
C.6d) | Battery charge/discharge rate: at least 1C | No
C.6e) | State max supported battery charge/discharge rate
C.6f) | State runtime at full load for base system (hours)
C.6g) | Charger capacity: batteries must be recharged to 90% capacity in 10 hours | No
C.6h) | State maximum charge current supported (Amps)
C.6i) | State rated number of full charge/discharge cycles (battery cycle life)
C.7 | Photovoltaic capabilities:
C.7a) | Dual MPPT charge controllers | No
C.7b) | 3 MPPT controllers preferred | No
C.7c) | Individual PV panel capacity: at least 450W | No
C.7d) | State maximum PV input current supported (Amps)
C.8 | Hard-wired output to client distribution board - sized to load requirements, supplied as part of electrical reticulation | No
C.8a) | Wire gauge of electrical cable according to system characteristics (amps, distance), best practice and manufacturer recommendation (CoC impact) | No
C.9 | The system must be wired by a certified electrician, who must issue an electrical compliance certificate (CoC) as part of the solution price | No
C.10 | System capacity:
C.10a) | State range of output sizes (KW) available for proposed system
C.10b) | State range of battery capacities (KWh) available for proposed solution
C.10c) | State range of PV capacities (KWp) available for proposed solution
C.11 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
C.11a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
C.12 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
D. | System Management
D.1 | Integrated remote management, configuration and monitoring functionality | No
D.1a) | Failure alerts and status warnings via SNMP, SMTP or other industry-standard mechanism preferred | No
D.1b) | Web standards-based remote management preferred | No
D.2 | User-accessible control panel for information, configuration and administration | No
D.3 | Monitoring and alerts:
D.3a) | Embedded sensors for all major components and inputs (e.g. temperature, grid, DC) | No
D.3b) | Status and performance metrics | No
D.3c) | Power status on different power sources (grid, PV, battery, etc.) | No
D.3d) | Component status/failures | No
D.3e) | Statistics and logs of system/power status over time | No
D.4 | Connectivity:
D.4a) | LAN, WLAN or WAN | No
D.4b) | USB or serial (RS-232/485) interface | No
D.4c) | CAN bus for communicating with system components | No
D.5 | State warranty terms for batteries
D.5a) | State the period for which the batteries are guaranteed unconditionally
D.6 | Security:
D.6a) | Support for physical and logical security | No
D.6b) | Password-protected remote monitoring | No
D.7 | Firmware and software updates (security and bug fixes) will be made available free of charge for the entire SLA period | No
D.8 | Documentation for complete solution with configuration and operation guidelines | No
E. | System enclosure and Environmental Characteristics
E.1 | System form factor: stand-alone, wall- or rack-mount | No
E.2 | Environmental sealing: dust- and water-proof to allow flexible deployment outside controlled environments if required - IP54 | No
E.3 | Power and cooling characteristics:
E.3a) | Grid power supply: 220/230 VAC ±10%, 50 Hz | No
E.3b) | Direct distribution board (DB) input and ouput | No
E.3c) | State overhead power consumption (Watts) for inverter (Overhead/Inefficiency = Total power draw - Output load) | 9999
E.3d) | Integrated cooling system to ensure reliable operation of all components) | No
E.4 | Safety features:
E.4a) | Surge protection | No
E.4b) | Overload protection | No
E.4c) | Over-temperature protection | No
E.4d) | Short-circuit protection | No
E.5 | Solution must be properly earthed and bonded according to SABS standards and industry best practices (CoC impact) | No
E.6 | Maximum acoustic noise level for base system: 65 dB(A) according to ISO 9296 (higher noise levels will be allowed for devices that significantly exceed specification) | No
E.6a) | State maximum noise level in dB(A) | 9999
F. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
F.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
F.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
F.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
F.3 | Only components that are supported by the OEM may be bundled with the solution | No
F.4 | High-level diagram of system architecture (showing major components and interfaces) must be included with submission | No
F.5 | Manufacturing certifications:
F.5a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
F.5b) | ISO 14001: certification for environmental management | No
F.5c) | Reduction of Hazardous Substances (RoHS) | No
F.5d) | State country of manufacture
F.6 | Electrical safety and EMC certifications for active components in solution (international certification acceptable):
F.6a) | Hardwired (DB-connected) systems must be installed according to SANS 0416 | No
F.6b) | All hardwired (DB-connected) systems must be installed by a qualified electrician, and a Certificate of Conformance (CoC) must be issued | No
F.6c) | Hardwired (DB-connected) systems must have a maintenance bypass switch installed as part of the solution | No
F.6d) | ISO/IEC 62368: Electrical safety | No
F.6e) | CISPR 32 / EN 55032: General EMC requirements | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | Section 2 contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
G. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
G.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
G.1a) | Base product _________________________________ | 999999.99
G.1b) | Component/Derivative 1 ________________________ | 0
G.1c) | Component/Derivative 2 ________________________ | 0
G.1d) | Component/Derivative 3 ________________________ | 0
G.1e) | Component/Derivative 4 ________________________ | 0
G.1f) | Component/Derivative 5 ________________________ | 0
G.1g) | Component/Derivative 6 ________________________ | 0
G.1h) | Component/Derivative 7 ________________________ | 0
G.1i) | Component/Derivative 8 ________________________ | 0
G.1j) | Component/Derivative 9 ________________________ | 0
G.1k) | Component/Derivative 10 _______________________ | 0
H. | Services
H.1 | Warranty extensions:
H.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
H.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1d) | Additional SLA/service option ____________________ | 0
H.1e) | Additional SLA/service option ____________________ | 0
H.1f) | Additional SLA/service option ____________________ | 0
H.1g) | Additional SLA/service option ____________________ | 0
H.2 | Installation charge for base eval config | 999999.99
H.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
H.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
I. | Additional Components
I.1 | Battery modules:
I.1a) | Battery module _______________________________ | 999999.99
I.1b) | Battery module _______________________________ | 999999.99
I.1c) | Battery module _______________________________ | 0
I.1d) | Battery module _______________________________ | 0
I.1e) | Battery module _______________________________ | 0
I.2 | PV panel modules:
I.2a) | PV module ___________________________________ | 0
I.2b) | PV module ___________________________________ | 0
I.2c) | PV module ___________________________________ | 0
I.2d) | PV module ___________________________________ | 0
I.2e) | PV module ___________________________________ | 0
I.3 | Remote management:
I.3a) | Management comms module _____________________ | 0
I.3b) | Other management module ______________________ | 0
I.3c) | Other management module ______________________ | 0
I.3d) | Other management module ______________________ | 0
I.4 | Software:
I.4a) | Software option _______________________________ | 0
I.4b) | Software option _______________________________ | 0
I.4c) | Software option _______________________________ | 0
I.4d) | Software option _______________________________ | 0
I.5 | Mounting solutions:
I.5a) | Rack-mount rails ______________________________ | 0
I.5b) | Wall-mount brackets ___________________________ | 0
I.5c) | Other mounting option __________________________ | 0
I.5d) | Other mounting option __________________________ | 0
I.5e) | Other mounting option __________________________ | 0
I.5f) | Other mounting option __________________________ | 0
I.6 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
I.6a) | Additional component __________________________ | 0
I.6b) | Additional component __________________________ | 0
I.6c) | Additional component __________________________ | 0
I.6d) | Additional component __________________________ | 0
I.6e) | Additional component __________________________ | 0
I.6f) | Additional component __________________________ | 0
I.6g) | Additional component __________________________ | 0
I.6h) | Additional component __________________________ | 0
I.6i) | Additional component __________________________ | 0
I.6j) | Additional component __________________________ | 0
I.6k) | Additional component __________________________ | 0
I.6l) | Additional component __________________________ | 0
I.6m) | Additional component __________________________ | 0
I.6n) | Additional component __________________________ | 0
I.6o) | Additional component __________________________ | 0
I.6p) | Additional component __________________________ | 0
I.6q) | Additional component __________________________ | 0
I.6r) | Additional component __________________________ | 0
I.6s) | Additional component __________________________ | 0
I.6t) | Additional component __________________________ | 0

## Gen1
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
Gen1: Entry-level generator solution
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Basic diesel generator solution. Designed, installed and maintained according to published Government electrical standards | No
A.1a) | Output capacity: 20KW or higher (solution must be sized to meet client's required output) | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Runtime: in case of grid power loss, the solution must maintain power to 25% of the full load for at least 12 hours | No
A.3a) | Diesel capacity: at least 12 hours (must be sized based on client's runtime requirement) | No
A.4 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.5 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Diesel generator as specified | No
B.3 | Automatic transfer switch (ATS) | No
B.4 | Management connection (LAN or WAN) | No
B.5 | Software included:
B.5a) | Status monitoring tools | No
B.5b) | Installation and configuration tools | No
B.5c) | Diagnostic and management tools | No
B.6 | Services included:
B.6a) | Solution sizing and design | No
B.6b) | On-site installation and configuration, including wiring into site distribution board | No
B.6c) | Integration into existing or supplied UPS | No
B.6d) | Certificate of Compliance (CoC) by qualified electrician | No
B.6e) | End-user training of at least 1-2 hours | No
B.6f) | Annual inspection and service of system to ensure optimum functioning for entire warranty period | No
C. | System Properties and Functionality
C.1 | In case of grid failure, system must automatically switch over to backup power (ATS) | No
C.1a) | State runtime at full load for base system (hours)
C.2 | Hard-wired output to client distribution board - sized to load requirements, supplied as part of electrical reticulation | No
C.2a) | Wire gauge of electrical cable according to system characteristics (amps, distance), best practice and manufacturer recommendation (CoC impact) | No
C.3 | The system must be wired by a certified electrician, who must issue an electrical compliance certificate (CoC) as part of the solution price. | No
C.4 | Support for single- or 3-phase solutions depending on end-user system requirements | No
C.5 | System capacity:
C.5a) | State range of output sizes (KW) available for proposed system
C.6 | Output waveform: pure sine wave | No
C.7 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
C.7a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
C.8 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
D. | System Management
D.1 | Integrated remote management, configuration and monitoring functionality | No
D.1a) | Failure alerts and status warnings via SNMP, SMTP or other mechanism | No
D.1b) | Web standards-based remote management | No
D.2 | Monitoring and alerts:
D.2a) | Embedded sensors for all major components and inputs (e.g. temperature) | No
D.2b) | Status and performance metrics | No
D.2c) | Component status/failures | No
D.2d) | Statistics and logs of system/power status over time | No
D.3 | User-accessible control panel for information, configuration and administration | No
D.4 | Physical fuel gauge for visual inspection | No
D.5 | Connectivity:
D.5a) | 10/100BT Ethernet port | No
D.6 | Security:
D.6a) | Support for physical and logical security | No
D.6b) | Password-protected remote monitoring | No
D.7 | Firmware and software updates (security and bug fixes) will be made available free of charge for the entire SLA period | No
D.8 | Documentation for complete solution with configuration and operation guidelines | No
E. | System enclosure and Environmental Characteristics
E.1 | System form factor: stand-alone with supporting infrastructure as required (e.g. roof or locked enclosure) | No
E.2 | Environmental sealing: dust- and water-proof to allow flexible deployment outside controlled environments if required - IP54 | No
E.3 | Power and cooling characteristics:
E.3a) | Generator must maintain 50Hz +- 1% under load during operation | No
E.3b) | Direct distribution board (DB) ouput | No
E.3c) | Integrated cooling system to ensure reliable operation of all components) | No
E.4 | Safety features:
E.4a) | Surge protection | No
E.4b) | Overload protection | No
E.4c) | Over-temperature protection | No
E.4d) | Short-circuit protection | No
E.5 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
E.6 | Maximum acoustic noise level for base system: 75 dB(A) according to ISO 9296 (higher noise levels will be allowed for devices that significantly exceed specification) | No
E.6a) | State maximum noise level in dB(A) | 9999
F. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
F.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
F.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
F.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
F.3 | Only components that are supported by the OEM may be bundled with the solution | No
F.4 | High-level diagram of system architecture (showing major components and interfaces) must be included with submission | No
F.5 | Manufacturing certifications:
F.5a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
F.5b) | ISO 14001: certification for environmental management | No
F.5c) | Reduction of Hazardous Substances (RoHS) | No
F.5d) | State country of manufacture
F.6 | Electrical safety and EMC certifications for active components in solution (international certification acceptable):
F.6a) | Hardwired (DB-connected) systems must be installed according to SANS 0416 | No
F.6b) | All hardwired (DB-connected) systems must be installed by a qualified electrician, and a Certificate of Conformance (CoC) must be issued | No
F.6c) | Hardwired (DB-connected) systems must have a maintenance bypass switch installed as part of the solution | No
F.6d) | ISO/IEC 62368: Electrical safety | No
F.6e) | CISPR 32 / EN 55032: General EMC requirements | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | Section 2 contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
G. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
G.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
G.1a) | Base product _________________________________ | 999999.99
G.1b) | Component/Derivative 1 ________________________ | 0
G.1c) | Component/Derivative 2 ________________________ | 0
G.1d) | Component/Derivative 3 ________________________ | 0
G.1e) | Component/Derivative 4 ________________________ | 0
G.1f) | Component/Derivative 5 ________________________ | 0
G.1g) | Component/Derivative 6 ________________________ | 0
G.1h) | Component/Derivative 7 ________________________ | 0
G.1i) | Component/Derivative 8 ________________________ | 0
G.1j) | Component/Derivative 9 ________________________ | 0
G.1k) | Component/Derivative 10 _______________________ | 0
H. | Services
H.1 | Warranty extensions:
H.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
H.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1d) | Additional SLA/service option ____________________ | 0
H.1e) | Additional SLA/service option ____________________ | 0
H.1f) | Additional SLA/service option ____________________ | 0
H.1g) | Additional SLA/service option ____________________ | 0
H.2 | Installation charge for base eval config | 999999.99
H.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
H.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
I. | Additional Components
I.1 | Remote management:
I.1a) | Management comms module _____________________ | 0
I.1b) | Other management module ______________________ | 0
I.1c) | Other management module ______________________ | 0
I.1d) | Other management module ______________________ | 0
I.2 | Software:
I.2a) | Software option _______________________________ | 0
I.2b) | Software option _______________________________ | 0
I.2c) | Software option _______________________________ | 0
I.2d) | Software option _______________________________ | 0
I.3 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
I.3a) | Additional component __________________________ | 0
I.3b) | Additional component __________________________ | 0
I.3c) | Additional component __________________________ | 0
I.3d) | Additional component __________________________ | 0
I.3e) | Additional component __________________________ | 0
I.3f) | Additional component __________________________ | 0
I.3g) | Additional component __________________________ | 0
I.3h) | Additional component __________________________ | 0
I.3i) | Additional component __________________________ | 0
I.3j) | Additional component __________________________ | 0
I.3k) | Additional component __________________________ | 0
I.3l) | Additional component __________________________ | 0
I.3m) | Additional component __________________________ | 0
I.3n) | Additional component __________________________ | 0
I.3o) | Additional component __________________________ | 0
I.3p) | Additional component __________________________ | 0
I.3q) | Additional component __________________________ | 0
I.3r) | Additional component __________________________ | 0
I.3s) | Additional component __________________________ | 0
I.3t) | Additional component __________________________ | 0

## Gen2
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
Gen2: Midrange generator solution
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Midrange diesel generator solution. Designed, installed and maintained according to published Government electrical standards | No
A.1a) | Output capacity: 30KW or higher (solution must be sized to meet client's required output) | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Runtime: in case of grid power loss, the solution must maintain power to 25% of the full load for at least 12 hours | No
A.3a) | Diesel capacity: at least 12 hours (must be sized based on client's runtime requirement) | No
A.4 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.5 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Diesel generator as specified | No
B.3 | Automatic transfer switch (ATS) | No
B.4 | Management connection (LAN or WAN) | No
B.5 | Software included:
B.5a) | Status monitoring tools | No
B.5b) | Installation and configuration tools | No
B.5c) | Diagnostic and management tools | No
B.6 | Services included:
B.6a) | Solution sizing and design | No
B.6b) | On-site installation and configuration, including wiring into site distribution board | No
B.6c) | Integration into existing or supplied UPS | No
B.6d) | Certificate of Compliance (CoC) by qualified electrician | No
B.6e) | End-user training of at least 1-2 hours | No
B.6f) | Annual inspection and service of system to ensure optimum functioning for entire warranty period | No
C. | System Properties and Functionality
C.1 | In case of grid failure, system must automatically switch over to backup power (ATS) | No
C.1a) | State runtime at full load for base system (hours)
C.2 | Hard-wired output to client distribution board - sized to load requirements, supplied as part of electrical reticulation | No
C.2a) | Wire gauge of electrical cable according to system characteristics (amps, distance), best practice and manufacturer recommendation (CoC impact) | No
C.3 | The system must be wired by a certified electrician, who must issue an electrical compliance certificate (CoC) as part of the solution price. | No
C.4 | Support for single- or 3-phase solutions depending on end-user system requirements | No
C.5 | System capacity:
C.5a) | State range of output sizes (KW) available for proposed system
C.6 | Output waveform: pure sine wave | No
C.7 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
C.7a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
C.8 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
D. | System Management
D.1 | Integrated remote management, configuration and monitoring functionality | No
D.1a) | Failure alerts and status warnings via SNMP, SMTP or other mechanism | No
D.1b) | Web standards-based remote management | No
D.2 | Monitoring and alerts:
D.2a) | Embedded sensors for all major components and inputs (e.g. temperature) | No
D.2b) | Status and performance metrics | No
D.2c) | Component status/failures | No
D.2d) | Statistics and logs of system/power status over time | No
D.3 | User-accessible control panel for information, configuration and administration | No
D.4 | Physical fuel gauge for visual inspection | No
D.5 | Connectivity:
D.5a) | 10/100BT Ethernet port | No
D.6 | Security:
D.6a) | Support for physical and logical security | No
D.6b) | Password-protected remote monitoring | No
D.7 | Firmware and software updates (security and bug fixes) will be made available free of charge for the entire SLA period | No
D.8 | Documentation for complete solution with configuration and operation guidelines | No
E. | System enclosure and Environmental Characteristics
E.1 | System form factor: stand-alone with supporting infrastructure as required (e.g. roof or locked enclosure) | No
E.2 | Environmental sealing: dust- and water-proof to allow flexible deployment outside controlled environments if required - IP54 | No
E.3 | Power and cooling characteristics:
E.3a) | Generator must maintain 50Hz +- 1% under load during operation | No
E.3b) | Direct distribution board (DB) ouput | No
E.3c) | Integrated cooling system to ensure reliable operation of all components) | No
E.4 | Safety features:
E.4a) | Surge protection | No
E.4b) | Overload protection | No
E.4c) | Over-temperature protection | No
E.4d) | Short-circuit protection | No
E.5 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
E.6 | Maximum acoustic noise level for base system: 75 dB(A) according to ISO 9296 (higher noise levels will be allowed for devices that significantly exceed specification) | No
E.6a) | State maximum noise level in dB(A) | 9999
F. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
F.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
F.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
F.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
F.3 | Only components that are supported by the OEM may be bundled with the solution | No
F.4 | High-level diagram of system architecture (showing major components and interfaces) must be included with submission | No
F.5 | Manufacturing certifications:
F.5a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
F.5b) | ISO 14001: certification for environmental management | No
F.5c) | Reduction of Hazardous Substances (RoHS) | No
F.5d) | State country of manufacture
F.6 | Electrical safety and EMC certifications for active components in solution (international certification acceptable):
F.6a) | Hardwired (DB-connected) systems must be installed according to SANS 0416 | No
F.6b) | All hardwired (DB-connected) systems must be installed by a qualified electrician, and a Certificate of Conformance (CoC) must be issued | No
F.6c) | Hardwired (DB-connected) systems must have a maintenance bypass switch installed as part of the solution | No
F.6d) | ISO/IEC 62368: Electrical safety | No
F.6e) | CISPR 32 / EN 55032: General EMC requirements | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | Section 2 contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
G. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
G.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
G.1a) | Base product _________________________________ | 999999.99
G.1b) | Component/Derivative 1 ________________________ | 0
G.1c) | Component/Derivative 2 ________________________ | 0
G.1d) | Component/Derivative 3 ________________________ | 0
G.1e) | Component/Derivative 4 ________________________ | 0
G.1f) | Component/Derivative 5 ________________________ | 0
G.1g) | Component/Derivative 6 ________________________ | 0
G.1h) | Component/Derivative 7 ________________________ | 0
G.1i) | Component/Derivative 8 ________________________ | 0
G.1j) | Component/Derivative 9 ________________________ | 0
G.1k) | Component/Derivative 10 _______________________ | 0
H. | Services
H.1 | Warranty extensions:
H.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
H.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1d) | Additional SLA/service option ____________________ | 0
H.1e) | Additional SLA/service option ____________________ | 0
H.1f) | Additional SLA/service option ____________________ | 0
H.1g) | Additional SLA/service option ____________________ | 0
H.2 | Installation charge for base eval config | 999999.99
H.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
H.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
I. | Additional Components
I.1 | Remote management:
I.1a) | Management comms module _____________________ | 0
I.1b) | Other management module ______________________ | 0
I.1c) | Other management module ______________________ | 0
I.1d) | Other management module ______________________ | 0
I.2 | Software:
I.2a) | Software option _______________________________ | 0
I.2b) | Software option _______________________________ | 0
I.2c) | Software option _______________________________ | 0
I.2d) | Software option _______________________________ | 0
I.3 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
I.3a) | Additional component __________________________ | 0
I.3b) | Additional component __________________________ | 0
I.3c) | Additional component __________________________ | 0
I.3d) | Additional component __________________________ | 0
I.3e) | Additional component __________________________ | 0
I.3f) | Additional component __________________________ | 0
I.3g) | Additional component __________________________ | 0
I.3h) | Additional component __________________________ | 0
I.3i) | Additional component __________________________ | 0
I.3j) | Additional component __________________________ | 0
I.3k) | Additional component __________________________ | 0
I.3l) | Additional component __________________________ | 0
I.3m) | Additional component __________________________ | 0
I.3n) | Additional component __________________________ | 0
I.3o) | Additional component __________________________ | 0
I.3p) | Additional component __________________________ | 0
I.3q) | Additional component __________________________ | 0
I.3r) | Additional component __________________________ | 0
I.3s) | Additional component __________________________ | 0
I.3t) | Additional component __________________________ | 0

## Gen3
SITA Certification: Infrastructure Solutions |  |  | Technical specification
This form must be filled in and submitted in Excel format |  |  | Version 2 - TU2, 2024-10-02
Gen3: Advanced generator solution
Line # | Specification | Response / OEM price incl. VAT | Comment / Details / Model #
Product brand name
Product name/model number
OEM or OEM representative
SECTION 1: TECHNICAL SPECIFICATION (Mandatory)
Note: | Section 1 specifies mandatory capabilities and components that must be supported and/or included with the offered solution (implemented and fully functional across all subsystems).
A. | Functional Requirements
A.1 | Advanced diesel generator solution. Designed, installed and maintained according to published Government electrical standards | No
A.1a) | Output capacity: 40KW or higher (solution must be sized to meet client's required output) | No
A.2 | Solution must be optimally sized and configured to suit the client's stated business requirement as defined in the request (RFP/RFQ) | No
A.3 | Runtime: in case of grid power loss, the solution must maintain power to 25% of the full load for at least 12 hours | No
A.3a) | Diesel capacity: at least 12 hours (must be sized based on client's runtime requirement) | No
A.4 | This specification is for a complete solution, provided by certified OEM partners, based on the stated client business requirement in an ad hoc RFP/RFQ. Complete solutions may include all accessories, upgrades and options listed below | No
A.5 | Warranty and support included in system price: countrywide on-site (repair or swap) with full coverage for entire system, including labour, hardware, software, upgrades and accessories, during office hours (7:30 - 17:00), with 4-hour acknowledgement and next business-day resolution (Zone-dependent according to Conditions) for 5 years (60 months) from date of delivery. OEM partner will be responsible for providing on-site services | No
B. | Standard Components (Included in Base Solution Price)
Note: | This section lists the components that must be included in the Base Price. All other components are priced separately in Section 2.
B.1 | Fully functional system as specified in Section 1, including hardware warranty, support SLA, standard power and interface cables, documentation, packaging and onsite delivery | No
B.2 | Diesel generator as specified | No
B.3 | Automatic transfer switch (ATS) | No
B.4 | Management connection (LAN or WAN) | No
B.5 | Software included:
B.5a) | Status monitoring tools | No
B.5b) | Installation and configuration tools | No
B.5c) | Diagnostic and management tools | No
B.6 | Services included:
B.6a) | Solution sizing and design | No
B.6b) | On-site installation and configuration, including wiring into site distribution board | No
B.6c) | Integration into existing or supplied UPS | No
B.6d) | Certificate of Compliance (CoC) by qualified electrician | No
B.6e) | End-user training of at least 1-2 hours | No
B.6f) | Annual inspection and service of system to ensure optimum functioning for entire warranty period | No
C. | System Properties and Functionality
C.1 | In case of grid failure, system must automatically switch over to backup power (ATS) | No
C.1a) | State runtime at full load for base system (hours)
C.2 | Hard-wired output to client distribution board - sized to load requirements, supplied as part of electrical reticulation | No
C.2a) | Wire gauge of electrical cable according to system characteristics (amps, distance), best practice and manufacturer recommendation (CoC impact) | No
C.3 | The system must be wired by a certified electrician, who must issue an electrical compliance certificate (CoC) as part of the solution price. | No
C.4 | Support for single- or 3-phase solutions depending on end-user system requirements | No
C.5 | System capacity:
C.5a) | State range of output sizes (KW) available for proposed system
C.6 | Output waveform: pure sine wave | No
C.7 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
C.7a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
C.8 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
D. | System Management
D.1 | Integrated remote management, configuration and monitoring functionality | No
D.1a) | Failure alerts and status warnings via SNMP, SMTP or other mechanism | No
D.1b) | Web standards-based remote management | No
D.2 | Monitoring and alerts:
D.2a) | Embedded sensors for all major components and inputs (e.g. temperature) | No
D.2b) | Status and performance metrics | No
D.2c) | Component status/failures | No
D.2d) | Statistics and logs of system/power status over time | No
D.3 | User-accessible control panel for information, configuration and administration | No
D.4 | Physical fuel gauge for visual inspection | No
D.5 | Connectivity:
D.5a) | 10/100BT Ethernet port | No
D.6 | Security:
D.6a) | Support for physical and logical security | No
D.6b) | Password-protected remote monitoring | No
D.7 | Firmware and software updates (security and bug fixes) will be made available free of charge for the entire SLA period | No
D.8 | Documentation for complete solution with configuration and operation guidelines | No
E. | System enclosure and Environmental Characteristics
E.1 | System form factor: stand-alone with supporting infrastructure as required (e.g. roof or locked enclosure) | No
E.2 | Environmental sealing: dust- and water-proof to allow flexible deployment outside controlled environments if required - IP54 | No
E.3 | Power and cooling characteristics:
E.3a) | Generator must maintain 50Hz +- 1% under load during operation | No
E.3b) | Direct distribution board (DB) ouput | No
E.3c) | Integrated cooling system to ensure reliable operation of all components) | No
E.4 | Safety features:
E.4a) | Surge protection | No
E.4b) | Overload protection | No
E.4c) | Over-temperature protection | No
E.4d) | Short-circuit protection | No
E.5 | Solution must be properly earthed and bonded according to SABS standards and industry best practices | No
E.6 | Maximum acoustic noise level for base system: 75 dB(A) according to ISO 9296 (higher noise levels will be allowed for devices that significantly exceed specification) | No
E.6a) | State maximum noise level in dB(A) | 9999
F. | Standards, Certifications and Compatibility
Note: | Proof of all certifications, accreditations and compliance with standards will be required at evaluation. Full test reports do NOT need to be submitted, except on request
F.1 | OEM certification: all installers/integrators of this product/system into Government must be trained and certified by OEM to supply, install and support the offered solution; appropriate accreditation for the level of skill required | No
F.1a) | Supply of products must be via the official local import channel, no grey market or alternative imports. All suppliers or integrators must be authorised by the OEM | No
F.2 | System must be installed strictly according to OEM standards and procedures by an OEM-authorised representative to conform to required performance and quality levels | No
F.3 | Only components that are supported by the OEM may be bundled with the solution | No
F.4 | High-level diagram of system architecture (showing major components and interfaces) must be included with submission | No
F.5 | Manufacturing certifications:
F.5a) | ISO 9001: certification for design, system and component manufacturing, and assembly | No
F.5b) | ISO 14001: certification for environmental management | No
F.5c) | Reduction of Hazardous Substances (RoHS) | No
F.5d) | State country of manufacture
F.6 | Electrical safety and EMC certifications for active components in solution (international certification acceptable):
F.6a) | Hardwired (DB-connected) systems must be installed according to SANS 0416 | No
F.6b) | All hardwired (DB-connected) systems must be installed by a qualified electrician, and a Certificate of Conformance (CoC) must be issued | No
F.6c) | Hardwired (DB-connected) systems must have a maintenance bypass switch installed as part of the solution | No
F.6d) | ISO/IEC 62368: Electrical safety | No
F.6e) | CISPR 32 / EN 55032: General EMC requirements | No
SECTION 2: PRICING SCHEDULE (OEM ceiling prices)
Note: | Section 2 contains mandatory pricing, including the system Base Price and components not included in the Base Price (see Section 1). All necessary cabling, drivers and mandatory accessories must be included in each component price. Value-added, non-mandatory components must comply with above specifications and be uniquely related to the offered system, with no conflicts or overlaps with other Items or Categories. These components are subject to SITA approval.
G. | Base system and Derivatives
Note: | Derivatives must be from the same product model line, e.g. alternative form factor or size, additional performance or functionality, and must meet all mimimum specifications
G.1 | Base Price(s) for offered system/product and derivatives, including all components specified as standard in Section 1:
G.1a) | Base product _________________________________ | 999999.99
G.1b) | Component/Derivative 1 ________________________ | 0
G.1c) | Component/Derivative 2 ________________________ | 0
G.1d) | Component/Derivative 3 ________________________ | 0
G.1e) | Component/Derivative 4 ________________________ | 0
G.1f) | Component/Derivative 5 ________________________ | 0
G.1g) | Component/Derivative 6 ________________________ | 0
G.1h) | Component/Derivative 7 ________________________ | 0
G.1i) | Component/Derivative 8 ________________________ | 0
G.1j) | Component/Derivative 9 ________________________ | 0
G.1k) | Component/Derivative 10 _______________________ | 0
H. | Services
H.1 | Warranty extensions:
H.1a) | Guaranteed 4-hour fix/replace, countrywide, 9 hours x 5 days | 999999.99
H.1b) | Guaranteed 8-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1c) | Guaranteed 4-hour fix/replace, countrywide, 24 hours x 7 days | 999999.99
H.1d) | Additional SLA/service option ____________________ | 0
H.1e) | Additional SLA/service option ____________________ | 0
H.1f) | Additional SLA/service option ____________________ | 0
H.1g) | Additional SLA/service option ____________________ | 0
H.2 | Installation charge for base eval config | 999999.99
H.3 | Hourly rate for additional installation services (over and above base eval config) | 999999.99
H.4 | Price for additional technical support per hour (excluding warranty or maintenance work) | 999999.99
I. | Additional Components
I.1 | Remote management:
I.1a) | Management comms module _____________________ | 0
I.1b) | Other management module ______________________ | 0
I.1c) | Other management module ______________________ | 0
I.1d) | Other management module ______________________ | 0
I.2 | Software:
I.2a) | Software option _______________________________ | 0
I.2b) | Software option _______________________________ | 0
I.2c) | Software option _______________________________ | 0
I.2d) | Software option _______________________________ | 0
I.3 | Additional solution components (these components must add value to and be related to the Item as specified). All offered components are subject to SITA approval:
I.3a) | Additional component __________________________ | 0
I.3b) | Additional component __________________________ | 0
I.3c) | Additional component __________________________ | 0
I.3d) | Additional component __________________________ | 0
I.3e) | Additional component __________________________ | 0
I.3f) | Additional component __________________________ | 0
I.3g) | Additional component __________________________ | 0
I.3h) | Additional component __________________________ | 0
I.3i) | Additional component __________________________ | 0
I.3j) | Additional component __________________________ | 0
I.3k) | Additional component __________________________ | 0
I.3l) | Additional component __________________________ | 0
I.3m) | Additional component __________________________ | 0
I.3n) | Additional component __________________________ | 0
I.3o) | Additional component __________________________ | 0
I.3p) | Additional component __________________________ | 0
I.3q) | Additional component __________________________ | 0
I.3r) | Additional component __________________________ | 0
I.3s) | Additional component __________________________ | 0
I.3t) | Additional component __________________________ | 0