## TU2 H2'24
Technical Specifications: Tech Update | [5 empty] | Date: 2024-09-27
Infrastructure Solutions (TU2, v2.0, H2 2024) | [5 empty] | Items: 31
Summary of Spec Changes
Changes are indicated by yellow blocks in the table. Changes include:
1. Added larger 3-phase UPS options for building and datacentre
2. Added Alternative Power solutions, including BESS & Generators
3. Bug fixes and small changes
Uninterruptible power supplies (UPS)
Single-phase UPS
| UPS_Li1 | UPS_Li2 | UPS_OL1 | UPS_OL2 | UPS_OL3
Profile | Entry-level line-interactive UPS | Midrange line-interactive UPS | Entry-level on-line UPS | Midrange on-line UPS | Advanced on-line UPS
Design | Line-interactive, pure sinewave |  | On-line double conversion, pure sinewave
Load supported1 | 800W | 1600W | 900W | 2700W | 4.5 KW +
Power rating | 1 KVA | 2 KVA | 1 KVA | 3 KVA | 5 KVA +
Efficiency | 80% |  | 90%
Runtime @ full load | 5 minutes
Max recharge time | 4 hours | 6 hours | 4 hours | 6 hours | 8 hours
Outputs | 4x C13 | 6x C13, 1x C19 | 4x C13 | 6x C13, 1x C19 | 6x C13, 1x C19 or hard-wired
Input tolerance (while bearing 50% load)2 | 160 - 270VAC, 50Hz ±2% |  | 120 - 270VAC, 50Hz ±15%
Management | USB/Serial, pref SNMP |  | USB/Serial, pref SNMP | USB/Serial, SNMP
Form factor | Rack-mount/Tower, pref convertible
Standards | IEC 60240-1, IEC 60240-2, pref IEC 60240-3, IEC 60240-4
OS certification | Windows, Linux |  |  | Windows, Linux, mainstream hypervisors
Support SLA | 5-year on-site, 4-hour response, NBD fix
3-phase UPS
| UPS_OL4 | UPS_OL5 | UPS_OL6
Profile | Advanced 3-phase on-line UPS | 3-phase building UPS | 3-phase datacentre UPS
Design | 3-phase input | 3-phase input + output
Load supported1 | 9 KW + | 45 KW + | 45 KW +
Power rating | 10 KVA + | 50 KVA + | 50 KVA +
Efficiency | 90%
Runtime @ full load | 5 minutes
Max recharge time | 10 hours
Outputs | Hard-wired
Input tolerance (while bearing 50% load)2 | 250 - 450VAC, 50Hz ±15%
Management | USB/Serial, SNMP
Form factor | Stand-alone
Standards | IEC 60240-1, IEC 60240-2, pref IEC 60240-3, IEC 60240-4
OS certification | Windows, Linux, mainstream hypervisors
Support SLA | 5-year on-site, 4-hour response, NBD fix
Equipment racks
| Rack_Wb | Rack_Net | Rack_Srv | Rack_Env | Rack_AV
Profile | Wall-mount cabinet | Network Cabinet | Server Rack | Environmental Rack | Audiovisual Rack
Rack units | 4 - 15 | 12 - 47 | 12 - 47 | 30+ | 12 - 47
Depth (mm) | 300+ | 600+ | 800+ | 800+ | 600+
Front & rear | Lockable | Lockable, 70% perforation option | Lockable, 70% perforated | Lockable Non-perforated | Lockable
Static ¦ dynamic load | 5kg/u ¦ - | 10kg/u ¦ 8kg/u | 20kg/u ¦ 15kg/u | 20kg/u ¦ 15kg/u | 10kg/u ¦ 8kg/u
Structural material | 16-gauge steel, powder-coated
Standards | IEC 60297-3 family, SANS (electrical), IP20
Support SLA | 5-year on-site, 4-hour response, NBD fix
Management and monitoring
| Env_Mon | Infra_Mgmt
Profile | Environmental monitoring | Infrastructure management tools
Standards | SNMP, SMTP, HTTPS, LDAP
Devices/systems | Data- & switching centre management and monitoring, incl. remote control, sensors, access control
Support SLA | 5-year on-site, NBD fix
Supporting Components and Services
Alternative power infrastructure
| BESS1 | BESS2 | BESS3 | Gen1 | Gen2 | Gen3
Profile | Entry-level BESS solution | Midrange BESS solution | Advanced BESS solution | Entry-level generator solution | Midrange generator solution | Advanced generator solution
AC load supported | 3KW | 5KW | 8KW | 20KW | 30KW | 40+KW
Storage capacity1 | 3KWh+ LiFePO4 batteries, 1C+ | 5KWh+ LiFePO4 batteries, 1C+ | 8KWh+ LiFePO4 batteries, 1C+ | Diesel storage up to 12 hours
Generation capacity2 | 3KWp+ Solar optional | 5KWp+ Solar optional | 8KWp+ Solar optional | 20KW | 30KW | 40+KW
Efficiency | 90% |  |  | -
Runtime @ 25% load | 4 hours |  |  | 12 hours before refuelling
Max recharge time | 12 hours |  |  | -
Output | Hard-wired into DB
Input tolerance | 210 - 260VAC, 50Hz ±2%
Management | Cloud / SNMP/SMTP pref |  |  | USB/Serial, SNMP + sensors + auto-start + monitoring service
Requirements | Designed, installed and maintained according to published SANS standards
IT facility infrastructure
| Ducting | Flooring | HVAC | Power | Fire
Profile | Ducting, trenching, routing | Raised flooring system | Cooling | Power distribution | Fire suppression
Requirements | Designed, installed and maintained according to published Government IT facility standards
Conditions/Notes
1. This Tech Update is to be implemented by H2 2024, and will remain in force until superseded by the next version.
2. Products are certified against the Detail Spec: Infrastructure, not this document. Make sure that the correct version of the detail spec is used for certifications and proposals (the spec header will indicate revision and TU).
3. This document indicates the base spec for Infrastructure, but it does not contain the detail specs, or requirements for upgrades or options. These can be found in the Detail Spec (see above).
4. Once these changes are implemented, the new baseline standard becomes mandatory, and all new products must comply.
5. As per the TCP, all OEMs are required to participate in the TU RFC process: non-response will be interpreted as agreeing with the proposed changes.
6. These specs are minimum requirements, therefore any proposal/capability that equals or improves on the spec will be acceptable.
7. "Pref/Preferred" indicates a non-mandatory requirement, or possible future direction.
Notes
1 Regardless of the KVA rating, the UPS must be sized to meet the specified Watts
2 Acceptable derating at lower voltages will be allowed
Notes
1 Battery storage must be configured on a per-project basis in terms of capacity and runtime.
2 Solar generation is an optional part of the solution, and can be configured on a per-project basis.
Notes:
1. This specification is subject to change based on Government requirements, and will be reviewed periodically.
2. The Technology Certification Process (TCP) requires OEMs to take the necessary actions in terms of ensuring product compliance with the new requirements, and certifying new products. OEMs and all other parties are requested to provide inputs and comments.
3. Products are certified against the Detail Technical Specification, not this document. All additional mandatory details, upgrades, components and more static specifications are contained in the Detail Spec. The TU document only captures the fast-changing specifications for technology management purposes. Detail Spec is available at www.sita.co.za/prodcert.htm
4. The fact that a product is certified does not necessarily mean it is available for procurement on a contract. In order for a product in this domain to be purchased via transversal contract, the product must be SITA-certified, and the supplier explicitly accredited on that contract (Contract RFB 2003 or relevant SITA panel in this case).